## Sipan School
Annex B: Bill of Quantities (BOQ) Rehabilitation Of Sipan School, Zakho Independent Adminstration, Iraq
1 All the work items should be done according to IRAQI General Technical Specifications (IGTS) that complies with ACI-Code 2005 applied according to the instructions of the supervisor Engineer. 2 All materials must be NEW, approved by supervisor Engineer. 3 All construction materials should be tested according to Construction Works Specification by NCCL (1981 edition), and (ASTM) specifications for water supply pipes. Supplier to cover the cost of lab tests. 4 The contractor Shall provide samples for all materials to be used in the project prior to using them in order to get approval from supervisor Engineer. 5 It is the duty of the contractor to check the designs for accuracy and adequacy, otherwise the Employer take no risk of the contractors failure to accomplish the work. 6 The contractor shall provide all required manpower, transportation, equipment, tools, machinery …etc. unless otherwise stated below. 7 In case of any difference between BOQ, designs and/or drawings; the instruction of supervisor Engineer will govern. 8 After all works finished the site must be cleaned from all debris and neglected materials must be removed to any where defined by municipality. 9 PREFABRICATED UNITS FOR THE ENGINEER : Constructing or providing caravans (with all necessary items) for Site Engineers’ Office, furniture and office equipment, including consumable materials, stationary, internet, maintenance of office and all requirements according to the request of Engineer including the landscape, park areas and etc. Supplying electricity, heating features and water as well as well air-conditioning till the end of Project are also included in the Unit Price.
TECHNICAL SPECIFICATIONS AND BILL OF QUANTITIES
No. | Item Description | Unit | Qty.
1 | Site Preparation: Providing tools,equipment and manpower for removing existing floor ceramic of WASH facilities and eastern latrine base, drinking area , The contractor shall demolish, break up and remove all temporary buildings, structures and superficial obstructions on the Site to place indicated by Municipality, repairing the damages caused by works for the existed infrastructures,The price includes cleaning the site from the debris as per instruction of engineers representative to a location identified by the local municipality. | M2 | 60
2 | Finishing works: Provide materials, labors, equipment, machines, curing and all requirements according to IGTS 100,1400,600 ,900 and instructions of supervising Engineer.
2.1 | Aluminum Doors: Provide and install reinforced Aluminum doors, the standard cross-section G-60, glass tined 6 mm and the filters between 6 mm . The work includes removing the existing doors repairing the door copen. The price includes supplying and fixing of all required, washers, locks, hinges, handles, Kylon, anti-fly mesh, and opening holes for discharging water.The work includes removing the existing ones, and repairing all defects if needed, All the work should be conducted according to instructions of the supervising engineer. | M2 | 25
2.2 | PVC Windows: Provide and install reinforced PVC windows, the standard cross-section thickness between (1.8mm to 2mm). The windows must be reinforced from inside by U section galvanized iron with a thickness not less than (0.8 mm). , single glass 6mm thickness with all required requirements. The price includes supplying and fixing of all required, washers, locks, hinges, handles, anti-fly mesh(fiber type) with PVC frame, and opening holes for discharging water, furthermore, the work includes removing the existing iron windows, welding works if needed, painting with two layers of oil paint the existing iron grill protection, the contractor should repair all finishing defect (windows copen, plaster, painting works) . All the work should be conducted according to the instructions of the supervising Engineer. | M2 | 65
2.3 | Oil Painting: Provide materials and all requirements for painting using oil paint for skirting inside (145cm) e of rooms corridors and (Betek, Polisan or equivalent) in three layers or more until the supervising engineer accepts the final appearance. the price includes removing and peeling the existing layer, sanding the surface until is the surface is clean to apply the new layer. All the works should be conducted according to IGTS and instructions of the supervisor Engineer. | M2 | 800
2.4 | False plastic Ceiling: Supply materials, tools, manpower for covering the roof of Sanitation units by (plastic boards) (60x60) cmx1.0 cm thickness,the price include hanging keels (Skka 38 mm) height every 120cm by screw, rod steel fisher, hanging rod 3mm, connecting the keels (Skka) 120cm,60cm long (32mm height ) -installation of plastic ceilling skirting (10x2) cm under the false ceiling on the circumference of all rooms , the measurement will be engineering square meter only all the work should be done according to the drawing and instructions of supervisor Engineer. | M2 | 80
2.5 | Supply of Shelves (2x0.45x2.5 m) : Providing Materials & labor for supplying and installing of wooden shelves for library with the (0.45m width x 2 m Length & 2.5 m height) using plywood 2.8 cm thick for the main frame and for shelves using (18mm MDF) , with all necessary works needed to fix the bookcase to the wall and floor, the works should be conducted according to the drawing and instructions of the supervising Engineer. | No. | 10
2.6 | Tilling works (Ceramic): supply materials, labors and equipment for tilling the floor of the WASH facilities and drinking areas with non slippery ceramic Tiles (40x40) cm, cement sand mortar 1:3 and adhesive materials if needed, with filing the tile joints with necessary white Cementous materials, the price include, cleaning the tiles, The work to be done according to the drawing and instructions of supervisor Engineer. | M2 | 60
3 | Sanitation works: Provide materials, labors, equipment, machines, curing and all requirements according to IGTS 1500 and instructions of supervising engineer.
3.1 | Eastern Latrine base: Provide all the materials, machines, and manpower needed to install new Ceramic pan eastern type with the flushing system (Siphon) (Turkuaz, Tota or equivalent) with all necessary fittings (gully trap, chromium water Valve No. 1, pipes fittings, specialglue,etc.).The work to be done according to the drawing and instructions of supervisor Engineer. | No. | 8
3.2 | Sanitation pipe PVC100 mm SN4, 3.5 mm: Provide all the materials, machines, and manpower needed for installing a 100 mm Sewerage lines by Excavation of trench min. (50 x 40) cm in concrete surface, removal of debris to the sites as directed by Engineer, compacting the bed spreading a layer of a clean soil under the pipe then laying and connecting the PVC pipes of Min.1% slope with special glue, white color (Size =100 mm, 4 mm wall thickness) with all necessary fittings and accessories (Tee, Elbow 45/90 degree, valves, divider, check points for (latrine, shower and kitchen) …etc.) and galvanized drain cover size (70x70mm) for the floor drain inside showers and Kitchens then backfilling with the top of the pipe by min. 10 cm of clean soil with proper compaction, and a layer of crushed gravel (10 cm), recasting by concrete the finishing floor in places needed according to the instruction of the supervising Engineer. | M.L | 50
3.3 | PVC manholes (500x500)mm: Provision of materials and manpower to install PVC manholes (50x50) cm with (HDPE) cover , for black & gray water from building to manholes. The work also includes excavation, covering the manholes by concrete 7 cm thickness (50 cm width), with all fitting and necessary work. | No. | 5
3.4 | Floor drain: Provision of materials, manpower and equipment to install stainless steel floor drain size (15x15) cm ,the work includes installing of PVC pipe 4" from the drain to manholes with required excavation works. The work includes back filling, all fitting, Gully Trap, hoses. According to the specification and instruction of supervisor Engineer. | No. | 8
3.5 | Stainless steel taps 1/2": Provision of materials and manpower to install new stainless taps size 1/2" according to the need with all fitting and necessary work. According to the specification and instruction of supervisor Engineer. | No. | 30
3.6 | Water Tanks: Provision and installation of (HDPE) water tanks with capacity not less than 1500 liters, approved sample vertical water tank with top/open cover, the walls with 3 Layers, of grey color internally and Blue color externally), and also with 1-inch cooper/brass outlet, 100% Virgin raw material not recycled (Polyethylene-linear high/low density) Food Grade. The tanks also should be Anti -ultra violet (U.V.) resistance which blocks the sunlight and sun heat free of Algae and odor. The work includes provision of float valve , also the work includes connection form the tank to the source of water using PPR Composite Water Pipes (size 25 mm) with Min. 3 Layers side walls (PPR/GF or AL/PE), PPR-C inner layer and a special mixture of GF PP or Aluminum middle layer and should be coated with an external layer of LDPE (Low Density of Polyethylene Layer) dark grey color to provide protection against ultraviolet rays, PN25 (approved sample and suitable for drinking purpose/food grade) and also installation of a valve with size 25 mm on the main pipe with 4 pieces of Stylophorum and wood 100x20x1000 mm as abase . All materials to be from approved quality & sample, and the supplier should provide certificate of origin and quality of all supplied materials. The work also includes fixing the tanks using a metallic chain or band, with all necessary work. | No. | 6
4 | External works: Provide materials, labors, equipment, machines, curing and all requirements according to IGTS and instructions of supervising engineer.
4.1 | Transferring fuel tank from ground floor to the 2nd floor(Roof):Provision of materials, manpower and equipments to transfere the fuel tanks (1000 ltr) (3 no.) with their existing iron bases to the roof of the school the work includes cleaning the roof, extending 1/2" pvc pipes (50 m.l) from the tanks to the ground floor with all required materials to complete the work (clips, elbows, valves, ..), according to the instruction of supervisor engineer. | LS | 1
5 | Electrical work : Electrical points including provision and installation of all materials and labor, wires 3x2.5 mm2 for powering and 3x1.5 mm2 for lighting, galvanized boxes, switch 15 amp. All the works shall be according to British Standards, Drawings and Section 1600 of I.G.T.S.
5.1 | Supplying, installing, connecting and checking an electrical main distribution board with dimensions (120 * 140) cm of plate with a thickness of 2mm , the work of an iron base for the board with a height of 30 cm contains: | LS | 1
5.2 | 3P MCCB , size 400 amp, 1pcs
5.3 | 3P MCCB , size 125 amp, 2pcs
5.4 | 3P MCCB , size 63 amp, 1pcs
5.5 | Ampere voltage and Hertz meter digital 1unit, with the CTs and indicator lamp 3 unit, and the price includes all accessories and according to the instructions and directions of the supervising engineer.
5.6 | Supplying and installing a secondary distribution board of capacity (18) lines with the main circuit breaker three-phase (60)amp and with circuit breakers of different size of Single Pole MCB with all necessary to work , the price include source cable 4*10mm2 (60m) Note: All board components must be ABB, Schneider, Fanar or equivalent type assembled by specialist With professional installation with inspection, commissioning . | Unit | 2
5.7 | Supplying, extending, and connecting a cable made of pure standard copper wire of size (3 x 4) mm² with all needed accessories from 18 line board to the classrooms and management rooms and according to the instruction of the electrical engineer supervising the work with the test and all that is necessary to work. | M.l | 700
5.8 | Supply and install suitable pvc trunk with all needed accessories using to handle and cover wires in ceiling and walls, the price include buried pipes for classrooms according to the instructions and directions of the supervising engineer. | LS | 1
5.9 | Supply and install suitable steel cable tray 10 cm with all needed accessories using to handle and cover wires in ceiling and walls according to the instructions and directions of the supervising engineer. | M.l | 100
5.10 | Supplying, installing, connecting, and checking wall-mounted fan using wire (3*1.5) mm2 inside a (25) mm PVC pipe with a regulator. The price includes all work requirements and according to the instructions and directions of the supervising engineer. | No. | 20
5.11 | Supplying, installing, connecting and checking spot light panel led type ( 72-96) watts with dimensions (60*60) cm (85v-265v) using a cable (3*1.5) mm2 with a switch on/off and the price includes all requirements Work according to the instructions and directives of the supervising engineer. | No. | 50
5.12 | Supplying, installing, connecting and checking led projector type 100 watts (85v-265v) waterproof using a cable (3*1.5) mm2 with a switch on/off and the price includes all requirements Work according to the instructions and directives of the supervising engineer. | No. | 2
5.13 | Supplying, installing, and checking waterproof wall bracket 20w (85v-265v) using wire (3*1.5) mm2 with switch on/off, and the price includes all work requirements and according to the instructions and directions of the supervising engineer. | No. | 20
5.14 | Supplying, installing, connecting and checking a 6 inch exhaust fan using wire (3 * 1.5) mm 2 inside with a switch on/off, and the price includes all work requirements and according to the instructions and directions of the supervising engineer. | No. | 4
5.15 | Supplying, installing, connecting and checking a 12 inch exhaust fan using wire (3 * 1.5) mm 2 inside with a switch on/off, and the price includes all work requirements and according to the instructions and directions of the supervising engineer. | No. | 2
5.16 | Supplying, installing, connecting and inspecting switch plug (13 amps) using a wire (3 * 2.5)mm2 , and the price includes all work requirements and according to the instructions and directions of the supervising engineer. | No. | 35
5.17 | Supplying, installing, connecting and operating the split units (inverter type Wall Mounted Split Unit) T3 comprissor , type (Gree, LG or equivalent) capacity of (2) tons of heating and cooling, using standard copper wires, (3*4) mm² inside a PVCTrank, the price include the on/off switch capacity (45) ampere with an indication lamp with the installation of the outdoor unit with plastic dampers floor on iron base with anti-rust paint and greasy dye, and with the establishment of pipes for condensation water and drainage to the nearest point of drainage, with a warranty for the conditioner for a period of 6 years and with all that is required to work according to the instruction of the supervising engineer. | Unit | 6
5.18 | Electricity Water Pump: Provide all the materials, machines, and manpower needed to install Electricity water pump size 2 HP with Automatic Powering instrument . The work includes all necessary fitting and connection with main electricity using cable 3x2.5 mm, installing steel box with lock for the pump . The supplier should provide certificate of origin and quality of all supplied materials according to IGTS and instructions of supervising Engineer.. | No. | 2
5.19 | Earth system: supply, install and connect an earhing for the whole school , contain (3 piece of 25mm dia /150cm length of pure Copper rods) connected by (1x50mm2) Cu wires, all connections should be bandaged by Copper welding or using Cu clamps, then to be connected through the same CU wire to the ground distribution bus bar of MDB, each rod should be buried in the excavated hole of (0.5 Wx3 Lx2 H) m, then back filled sequence by (coal, salt, bentonite clay) with providing plastic manhole for each rod . | Set | 1
5.20 | Anti lightning : Supply, install and connect anti lightning system of type (Early streamer emitter (ESE) ,using suitable 6m GS pole ,including (3 * (16mm-25mm) dia /150cm length of pure Copper rods) connecting by (1x50mm2) Electrolytic Copper Conductor, ,Exothermic welding way should be use. Back filling sequence by (coal, salt),Lightning system is active Type the radius of protection shall cover all the Plant and work must done according to the supervisor engineer's instruction | Set | 1
6 | Sound System
6.1 | Supplying, installing, connecting and checking an original 500watt amplifier(sound) device of Panasonic, Sony, or equivalent. The price includes the microphone and with all work requirements and according to the instructions and directives of the supervising engineer. | LS | 1
6.2 | Supplying, installing, connecting and checking 8 watt speaker installed in the ceiling using a wire size (3 * 0.75) mm2 and the price includes all work accessories and according to the instructions and directions of the supervising engineer. | No. | 25
6.3 | Supplying, installing and checking a large electric bell for the school using wire (3 * 1.5) mm2 with push button switch , and the price includes all work requirements and according to the instructions and directions of the supervising engineer. | No. | 1
7 | Monitoring Camera CCTV
7.1 | Supplying, installing, connecting and checking HD CAMERA 4MP surveillance camera. The price includes a CAT6 cable extension. With a plastic box and all work requirements and according to the instructions and directions of the supervising engineer | No. | 8
7.2 | Supplying, installing, connecting and checking the 4KS2-Digital video recorder - NVR 32 channel, and the price includes all work requirements and according to the directions and instructions of a supervising engineer | No. | 1
7.3 | Supplying, installing and connecting a 4TB HDD storage disk | No. | 2
7.4 | Supplying, connecting and checking the HDMI cable, and the price includes all work requirements and according to the instructions of the supervisor engineer | No. | 2
7.5 | Supplying, extending, connecting and checking switch 24 port, and the price includes all work requirements and according to the instructions and directions of the supervisor engineer | No. | 1
7.6 | Supplying and installing the Rack 4 unit, and the price includes all work requirements and according to the directions and instructions of a supervising engineer | No. | 1
7.7 | Supplying, installing, connecting and checking inverter 2000 w, and the price includes all work requirements and according to the instructions and directives of a supervising engineer. | No. | 1
7.8 | Supplying, installing, connecting and checking Battery 100Ah. The price includes all work requirements and according to the instructions and directives of a supervising engineer. | No. | 2
8 | Data Show
8.1 | Supplying, installing, connecting a datashow with all needed accsessories and cables the price includes all work requirements and according to the instructions and directives of a supervising engineer | No. | 10