## WAVING CENTER-Electrical
UNHCR PAKISTAN
CONSTRUCTION OF PREFABRICATED COOPERATIVE MODEL (WEAVING CENTER) IN KP
ENGINEER'S ESTIMATE
ELECTRICAL WORKS
ITEM No. | KPK MRS 2022 REF. NO. / NS (2nd BI ANNUAL) | DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) | (e) | (f) | (g)
A. |  | SCHEDULED ITEMS
FANS & EXHAUST FANS
E-01 | 15-68-c | Supply and Erection best quality AC ceiling fan complete with GI rod, canopy, blades & regulator: 56" sweep. | Each | 1 |  | 0
E-02 | 15-69-a | Supply & Erection best quality exhaust fan complete with shutter & regulator: 12" sweep. | Each | 30 |  | 0
E-03 | 15-77-c | Supply and Fixing electric AC exhuast/fresh air circulation(double way) 220/230 single phase plastic frame body and blade complete 12"x12" | Each | 6 |  | 0
E-04 | 15-67 | Making hole in wall with necessary masonry work for exhaust fan any size complete | Each | 36 |  | 0
E-05 | 15-78 | Supply and Fixing of 18" dia Direct axial Wall Bracket fan,1450Rpm, Max 50db sound level Fan shall be made with 99% purity Copper windings | Each | 70 |  | 0
E-06 | 15-25 | Supply and Erection girder clamp hook, 5/8" dia.for hanging ceiling fans. | Each | 1 |  | 0
NOTE:The contractor/supplier shall ensure that the supplied fans are wound with pure 99.9% pure enamelled copper winding.The core of the fans shall be made from grain oriented electrical steel sheet.The exhaust fans shall follow the same standards described above. Moreover all fans should be NEECA approved.The fans shall be installed at the bottom level of structural beams. The contractor is required to get the approval from the site staff.
CIVIL WORKS FOR CABLES
E-07 | 03-51 | Excavation of trench in all kinds of soils except cutting in rock for pipelines upto 1.5m depth (for electrical cables) | 1000 Cft | 18000 |  | 0
E-08 | 03-67-c | Structural backfill using Common Material available at site. | 1000 Cft | 10000 |  | 0
E-09 | 07-30 | Supplying and filling sand under floor or plugging in wells | 100 Cft | 10000 |  | 0
NOTE:
The above items must be executed as follows:
| a) | Excavation in all kind of material including back filling, compaction, layer of bricks 9" in width and warning tape for lighting cables trench width 3' & height 4' complete in all respect as per specifications and as directed by the Engineer .
CABLE PULLING PIT ( 2'x2'x3')
E-10 | 03-49-a | Excavation in open cut for sewers & manhole except shingle, gravel & rock : Upto 2m (for electrical works) | 1000 Cft | 350 |  | 0
E-11 | 03-67-c | Structural backfill using Common Material available at site. | 1000 Cft | 350 |  | 0
E-12 | 06-05-i | Plain Cement Concrete incl. placing, compacting, finishing & curing (Ratio 1:4:8) | 100 Cft | 20 |  | 0
E-13 | 06-07-a-03 | RCC in roof slab, beam, column & other structural members, insitu or precast. Type C (1:2:4) | 100 Cft | 140 |  | 0
E-14 | 06-08-c | Supply & fabricate M.S. reinforcement for cement concrete (Hot rolled deformed bars Grade 40) | 100 Kg | 317.6044 |  | 0
E-15 | 11-08-b | Cement plaster 1:3 upto 20' height 1/2" thick | 100Sft | 152 |  | 0
E-16 | 07-30 | Supplying and filling sand under floor or plugging in wells | 100 cft | 350 |  | 0
E-17 | 24-33-d | Supplying and fixing, cast iron manhole cover with frame, etc. (Heavey Type) of approved quality complete. 24" (600 mm) dia | Each | 6 |  | 0
NOTE:
The above items must be executed as follows:
| a | Cable pulling pit (2'-0" X 2'-0" X 3') made of RCC walls(1:2:4) and CI cover with MS angle frame for easy pulling of LT cables and telephone/networking cables including all accessories located as per drawings.
LT CABLES
E-18 | 15-122-f | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (50 sqmm, 4 core ) for Power DB | RM | 150 |  | 0
E-19 | 15-122-d | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (25 sqmm, 4 core ) | RM | 30 |  | 0
E-20 | 15-122-c | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (16 sqmm, 4 core ) | RM | 50 |  | 0
E-21 | 15-122-b | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (10 sqmm, 4 core) For Lights DB | RM | 50 |  | 0
E-22 | 15-122-a | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (6 sqmm, 4 core ) (for pumps). | RM | 100 |  | 0
E-23 | 15-07-d | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 19/0.083" (70mm2) (For Smdb) | RM | 50 |  | 0
E-24 | 15-07-c | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 19/0.064" (35mm2 as ECC) | RM | 10 |  | 0
E-25 | 15-07-b | Supply and Erection single core PVC insulated & sheathed copper conductor, 660/1100V cable : 19/0.052" (25mm2 as ECC) For Power DB | RM | 30 |  | 0
E-26 | 15-06-f | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.064" (16mm2 as ECC) | RM | 110 |  | 0
E-27 | 15-06-e | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.044" (6mm2 as ECC) | RM | 150 |  | 0
E-28 | 15-124-a | Supply and Erection of 2 X 10 sqmm copper cable | RM | 10 |  | 0
E-29 | 15-126-a | Supply at site, installation, testing and commissioning of PVC insulated un-armoured copper conductor cable 600 / 1000 Volt grade (or otherwise mentioned in cable description ) in prelaid conduits / trenches to be installed as per routes shown on drawings including cost of all necessary materials, connections, identification tags, cables lugs properly crimped at both ends for the following sizes complete in all respects (10sqmm, 1 core ) . | RM | 50 |  | 0
CONDUITS & PIPES
E-30 | 15-02-b-06 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 2" i/d | Rft. | 550 |  | 0
E-31 | 15-02-b-05 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1.5" i/d | Rft. | 100 |  | 0
E-32 | 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d | Rft. | 10000 |  | 0
E-33 | 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d | Rft. | 4000 |  | 0
E-34 | 15-79-a | Supply and Fixing PVC conduit for surface wiring (duraduct) 1/2" including all charges for nail screws etc | Rft. | 50 |  | 0
E-35 | 15-79-b | PVC conduit for surface wiring (duraduct) 1" including all charges for nail screws etc | Rft. | 50 |  | 0
E-36 | 15-79-c | PVC conduit for surface wiring (duraduct) 1.5" including all charges for nail screws etc | Rft. | 50 |  | 0
E-37 | 15-79-d | PVC conduit for surface wiring (duraduct) 2" including all charges for nail screws etc | Rft. | 50 |  | 0
E-38 | 24-18-c-05 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured) jointed with socket, elbow, tee, bend and plug bend etc.manufactured by the respective manufacturer complete as per specifications. uPVC Pressure Pipes Class D (12 Bar) 3" Nominal Pipe Size (NPS) | Rft. | 1000 |  | 0
E-39 | 24-18-c-03 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured) jointed with socket, elbow, tee, bend and plug bend etc. manufactured by the respective manufacturer complete as per specifications. uPVC Pressure Pipes Class D (12 Bar) 2"Nominal Pipe Size (NPS) | Rft. | 500 |  | 0
E-40 | 24-18-c-06 | Providing, laying, cutting, jointing, testing and disinfecting UPVC pressure pipeline in trenches (conforming to BS 3505 manufactured ) jointed with socket, elbow, tee, bend and plug bend etc.manufactured by the respective manufacturer complete as per specifications. uPVC Pressure Pipes Class D (12 Bar) 4" Nominal Pipe Size (NPS) | Rft. | 1000 |  | 0
WIRING ACCESSORIES
E-41 | 15-127-a | Supply at site, installation, testing and commissioning of the One gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | No. | 3 |  | 0
E-42 | 15-127-b | Supply at site, installation, testing and commissioning of Two gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | No. | 3 |  | 0
E-43 | 15-127-c | Supply at site, installation, testing and commissioning of Three gang light control switches 10 Amps, 250Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | No. | 3 |  | 0
E-44 | 15-127-d | Supply at site, installation, testing and commissioning of Four gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | No. | 15 |  | 0
E-45 | 15-127-e | Supply at site, installation, testing and commissioning of Five gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects. | No. | 5 |  | 0
E-46 | 15-127-f | Supply at site, installation, testing and commissioning of Six gang light control switches 10 Amps, 250 Volts one way, including appropriate size concealed MS, powder coated back box, complete in all respects | No. | 40 |  | 0
E-47 | 15-127-h | Supply at site, installation, testing and commissioning of One gang light control switches 10 Amps, 250Volts two way, including appropriate size concealed MS, powder coated back box, complete in all respects | No. | 4 |  | 0
E-48 | 15-156 | Supply, Installation, Connecting, testing and commissioning of 400 watt Fan dimmer, polycarbonate flame retardant with fancy gang plate fixed on die fabricated poweder coated metal board recessed in wall or column , Complete in all respects | No. | 5 |  | 0
E-49 | 15-155-c | Supply, installation, connecting, testing & commissioning of flush type 13 Amps 3-pin simplex outlet with 3 pin switch and socket combine unit with neon bulb fixed on plastic or fiber top covered, including 14 SWG metal board with earth | No. | 105 |  | 0
E-50 | 15-127-j | Supply at site, installation, testing and commissioning of 3 pin switched socket unit 13/15 Amps, 250Volts, round pin including appropriate size MS, powder coated back box, complete in allrespects. | Each | 25 |  | 0
E-51 | 15-127-n | Supply at site, installation, testing and commissioning of DP switch 20 Amps with neon indication lamp complete with MS, powder coated back box, complete in all respects. | Each | 25 |  | 0
WIRING IN CONCEALED CONDUITS
E-52 | 15-06-a | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 3/0.029"(1.5mm2). | Rft | 30000 |  | 0
E-53 | 15-06-c | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.029"(2.5mm2) . | Rft | 25000 |  | 0
E-54 | 15-06-d | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.036"(4mm2) . | Rft | 13000 |  | 0
E-55 | 15-06-e | Supply and Erection single core PVC insulated+sheathed copper conductor 250/440 V grade cable : 7/0.044"(6mm2) . | Rft | 500 |  | 0
E-56 | 15-02-b-03 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 1" i/d (for wiring) | Rft. | 5000 |  | 0
E-57 | 15-02-b-02 | Supply and Erection PVC pipe for wiring purpose complete Recessed in walls including chase etc : 3/4" i/d (for wiring) | Rft. | 14000 |  | 0
NOTE: The wiring shall be done as following.
| a | Wiring of light circuit from Distribution Board to switch, including circuit wiring between switches on the same circuit with Two nos. single core 2.5 Sqmm and One no.1.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1 " PVC conduits including PVC conduit, conduit accessories (junction box, pull box, metal fan box etc) complete in all respects.
| b | Wiring from switch to light or fan point (1 way / 2 way) with 3 Nos. single core 1.5 Sqmm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit including PVC conduit, conduit accessories (junction box, pull box, metal fan box etc) complete in all respects.
| c | Wiring from light to light with 3 Nos. single core 1.5 Sqmm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 3/4" PVC conduit including PVC conduit, conduit accessories (junction box, pull box, metal fan box etc) complete in all respects.
| d | Wiring of circuit from Distribution Board to 13A , 230 Volts, 3 pin switched socket outlet with Two nos. single core 4 sqmm and One no. 2.5 sqmm PVC insulated 300/500 Volts grade stranded copper conductor cables in 1" dia concealed PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects.
| e | Wiring from 13 Amps, 3 pin socket to socket with Two nos. single core 2.5 Sqmm and One no. 1.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc.complete in all respects.
| f | Wiring of circuit from distribution board to 15A, 230 Volts, 3 Pin switched socket outlet with 2 Nos. one core 4 Sqmm and One no. 2.5 sq mm PVC insulated 300/500 Volts grade copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects.
| g | Wiring from 15 Amps, 3 pin socket to socket with Two nos. single core 2.5 Sqmm and One no. 1.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc.complete in all respects.
| h | Wiring of circuit from distribution board to 20A, 230 Volts, switched socket outlet with 2 Nos. one core 4 Sqmm and One no. 2.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects (For ACs).
| i | Wiring of circuit from distribution board to 20A, 230 Volts, switched socket outlet with 2 Nos. one core 6 Sqmm and One no. 2.5 sq mm PVC insulated 300/500 Volts grade stranded copper conductor cables in concealed 1" PVC conduit laid underfloor including PVC conduit, conduit accessories, etc. complete in all respects (For Electric Water heaters).
NOTE: PVC pipes & all its accessories shall not catch/support fire. 1.5mm2 (3/0.029) & 2.5mm2 (7/0.029) single core cables are stranded having 3 strands & 7 strands respectively.
LIGHTNING PROTECTION SYSTEM
E-58 | 15-43-a | Supply and erection of copper tape, including copper staple, copper nails/Screw etc.: Size (1.5"x1/8") | Rft. | 800 |  | 0
E-59 | 15-42-e | Supply, Installation, Testing and Commissioning of Air terminal or arrester | Each | 4 |  | 0
E-60 | 15-106 | Supply, installation, testing & commissioning of Lightning Protection System | Each | 4 |  | 0
LIGHT FIXTURES
E-61 | 15-36-k-02 | Supply, installation, connecting, testing and commissioning of Surface mounting LED tube light with 1x2000 lumens output and fixture, complete in all respects | No. | 10 |  | 0
E-62 | 15-36-i-10 | Supply, installation, testing and commissioning of 1x6 Watt LED BULKHEAD light fixture, of best quality. | Each | 40 |  | 0
E-63 | 15-36-i-7 | Supply, installation, testing and commissioning of 1x23 Watt, E-27 base, wall bracket light, complete in all respects. | Each | 5 |  | 0
E-64 | 15-36-j-12 | Supply, installation, connecting, testing & commissioning of 10W LED Down Light Fixture suitable for 1300 lux, as per instruction of Engineer, surface mounted circular shape or equivalent | No. | 50 |  | 0
STRUCTURED CABLING SYSTEM (TELEPHONE & NETWORKING)
E-65 | 15-138-e-01 | Supply, Installation, testing and commissioning of Single Port Data outlet of 1 x RJ-45 I/Os for Cat-6 cable and with 16 SWG back box, complete in all respects | Each | 10 |  | 0
E-66 | 15-138-e-02 | Supply, Installation, testing and commissioning of Dual Port Data outlet of 1 x RJ-45 I/Os for Cat-6 cable and with 16 SWG back box completed in all respect | Each | 10 |  | 0
E-67 | 15-138-g | Supply and Erection of 3M Cat-6 Cable in 3/4",1"pvc conduit, complete in all respect | Rft | 3000 |  | 0
E-68 | 15-141-a | Supply, installation, testing and commissioning of Cable Manager / Organizer Black, 1pc, Black. | Each | 1 |  | 0
B. |  | MISCELLANEOUS ITEMS
E-69 | 15-178 | Supply & Erection of TV socket | Each | 4 |  | 0
E-70 | 15-175 | Supply & Erection of TV/satellite cable complete | Each | 4 |  | 0
E-71 | 15-135-d | Supply at site, fabrication and installation of GI perforated cable tray 16 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(150X100mm) | Rft. | 300 |  | 0
E-72 | 15-135-b | Supply at site, fabrication and installation of GI perforated cable tray 16 SWG 8 ft. to 10 ft. long with sides 3" high to be installed on wall, or in vertical, or above false ceiling in horizontal position or floor mounted or as shown on drawing, including cost of hanging arrangement brackets made of angle iron 38mm x 38mm x 6mm installed at every 3 ft., cost of all necessary fixing accessories, complete in all respects.(300X100mm) | Rft. | 300 |  | 0
C. |  | SOLAR SYSTEM (PHOTOVOLTAIC)
Note: Mounted structure for the solar panels will be at 10 feet High for the parking area
E-73 | 26-01-d-01 | Supply and Erection of Solar PV Module (Solar Panel) Mono-crystalline A-Grade (per Watt) (As per Approved Specifications) | Watt | 100000 |  | 0
E-74 | 26-01-f-06 | Supply and Erection of 12 V Lithium LiFeP04 battery per KWhr | KWhr | 120 |  | 0
E-75 | 26-01-i-06 | Supply and Erection of On Grid Hybrid inverter | Per Watt | 100000 |  | 0
E-76 | 26-01-o | Supply and Erection of BOX / STAND for Batteries SHS Inverter & Charge Controller | Watt | 100000 |  | 0
E-77 | 26-01-n-03 | Supply and Erection of Stainless Steel Nuts and Bolts | Watt | 100000 |  | 0
E-78 | 26-01-m-01 | Supply and Erection of hot dipped (80 microns Average) galvanized steel of minimum thickness of 12 SWG / 2.64 mm Channel / Pipe or 8 SWG /4.06 mm Angle | Per Watt | 100000 |  | 0
E-79 | 26-01-n-02 | Supply and Erection of 1x1 ft 4mm Copper Earthing Plate | Watt | 100000 |  | 0
E-80 | 26-01-n-01 | Supply and Erection of Copper Conductor of 10 AWG | Watt | 100000 |  | 0
E-81 | 26-01-j-02 | Supply and Erection of dV /dT or Sine Filter ordV/dT filter 22 KW to 45 KW | No | 2 |  | 0
E-82 | 26-01-h-01 | Supply and Erection MC4 connector (TUV Approved) | Pair | 100 |  | 0
E-83 | 26-01-h-02 | Supply and Erection MC4 Branch connector | Pair | 100 |  | 0
E-84 | 26-01-g-09 | Supply and Erection 2x4 sq.mm flexible copper cable | Rft | 1500 |  | 0
E-85 | 26-01-g-10 | Supply and Erection 2x6 sq.mm flexible copper cable | Rft | 1500 |  | 0
E-86 | 26-01-g-11 | Supply and Erection 2x10 sq.mm flexible copper cable | Rft | 1500 |  | 0
E-87 | 26-01-g-12 | Supply and Erection 2x16 sq.mm Copper cable | Rft | 500 |  | 0
E-88 | 26-01-g-13 | Supply and Erection 2x25sq.mm Copper cable | Rft | 500 |  | 0
E-89 | 26-01-g-14 | Supply and Erection 2x35 sq.mm Copper cable | Rft | 500 |  | 0
EARTHING SYSTEM
E-90 | 15-105-f | Supply and Erection of Grounding connecting points | Each | 6 |  | 0
Total Cost of Scheduled Items (Rs.) | [5 empty] | 0
D. |  | NON-SCHEDULED ITEMS
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per specifications and as approved by the Engineer.
LT DISTRIBUTION BOARD
(Ref. Specification Section-8001, 8133)
LT 415V AC Main DB/Sub-Main DBs shall be made from 14 SWG sheet steel, while all other DBs must be of 16SWG. This shall be designed, fabricated and manufactured as a free standing floor type. The sheet metal work shall be cleaned down to bare shining metal degreased, derusted and painted with TWO base coats of antirust RED paint. The sheet metal work shall be finished in TWO coats of powder paint. The color and shade shall be as approved by the Engineer. The distribution Board shall be complete with all internal wirings, tags, identification labels, TPN and E copper busbars, accessories etc. The DB should be provided with the armored glands. The bus-bars shall be insulated in RED, YELLOW, BLUE and BLACK insulations. The insulation shall be heat shrinkable type or as directed by the Engineer.
E-91 | NS-01 | MSB | Job | 1 |  | 0
E-92 | NS-02 | DB-LIGHTS/FANS/POWER | Job | 1 |  | 0
E-93 | NS-03 | DB-AC | Job | 1 |  | 0
E-94 | NS-04 | DB-EXT | Job | 1 |  | 0
E-95 | NS-05 | SOLAR DB | Job | 1 |  | 0
NOTE: Cable Glands should be of non-magnetic material i.e. Stainless Steel or Aluminum
LIGHT FIXTURES
(Ref. Specification Section-8001, 8150)
Following light fixtures installed on surface or wall or floor or false ceiling or columns or masts complete with all accessories such as lamps, lamp holders, ballasts, starters, ignitors, capacitors, LED drivers as applicable, etc. including all relevant installation material as required and approved by the Engineer. (Note: The contractor shall be reponsible for compatibility of recessed mounted light fixtures with gypsum / aluminium / dampa etc., false ceiling types in coordination with architectural design.)
E-96 | NS-06 | Surface mounted LED batten Light Fixture (600mm) with minimum 800 lumens , fixed output LED driver and prismatic diffuser, IP20 rated (To be used in Toilets vanities). | No. | 6 |  | 0
E-97 | NS-07 | 15 W Recessed LED downlight of warm white color with integrated driver and frosted glass diffuser , IP20, or better | No. | 20 |  | 0
E-98 | NS-08 | Surface/Recessed Panel type LED light fixture (600mm by 600 mm) suitable for 2' x 2' false ceiling with minimum 3700 lumens IP20 rated. | No. | 130 |  | 0
EARTHING SYSTEM
(Ref. Specification Section-8001, 8240)
E-99 | NS-09 | Earth Electrode for earthing shall comprise of 75 mm x 4877 mm x 6 mm thick copper plate with 4 Nos. 6 mm dia brass nuts, bolts and washers 70 sqmm HDHC Copper wire as earthing leads.
A 100 mm dia Medium Duty GI pipe shall be used with 10 mm dia holes @500 mm c-c. The total length of this GI pipe should be 45 ft.
A 150 mm dia 80 ft long hole should be drilled in ground by percussion method and above mentioned 100 mm dia medium duty GI pipe should be fixed in this hole simultaneously up to the depth of 60 ft from NSL.
When the drilling up to 80 ft depth is complete, The above mentioned earth electrode shall be drop down to the bottom of the hole with the help of 2 Nos 70 sqmm earth leads.
|  | Once the plate is in place fill in the hole with moisture retaining bentonite slurry with tremie method up to the top. When the bentonite settle down cast a (1:4:8) concrete manhole 700 mm x 700 mm & 500 mm deep as shown in the drawing. Place a medium duty CI cover as shown in the drawing. | Job | 8 |  | 0
STRUCTURED CABLING SYSTEM (TELEPHONE & NETWORKING)
(Ref. Specification Section-8001, 8312)
E-100 | NS-10 | Supply, Installation & Connecting up of UTP- Cat-6,steel Frame Patch Panel with 24 port modular UTP - Cat-6, Loaded with BLUE CAT I/O UTP , Keystone Jacks Toolless, Support 1.0 Gigabit Network including rear cable management | No. | 1 |  | 0
E-101 | NS-11 | Supply, Installation of UTP - Cat-6, Patch Cords Support 1.0 Giga Network at 250 Mhz machine made. Installed between patch panel & Network switch and face plate (Blue for Data , Red for VOIP) .
| i) | 1.0 m Length | No. | 10 |  | 0
| ii) | 3.0 m Length | No. | 10 |  | 0
E-102 | NS-12 | Supply, Installation of wall mounted 6U (600 x 550mm) data cabinet imported, double section, including fans with lockable front glass door two side opening, 04 Way power distribution unit rack mounted IP 20. | No. | 1 |  | 0
IP CCTV SYSTEM
(Ref. Spec. Nos. 8001, 8335)
E-103 | NS-13 | Supply at site, installation, testing & commissioning of Network TDN WDR IR Rugged Dome/Bullet Camera, 1/2.9" CMOS, 4 MP, 2.7-12mm MFZ, 4 High Power LEDs,VARIFOCAL DC IRIS NS, PoE, H.264, microSD, 128 GB max, IP 54 or better,IK 10, built in cyber security feature including mounting bracket, all fixing and mounting accessories, complete in all respects., complete in all respects. | Each | 30 |  | 0
MISCELLANEOUS ITEMS
(Ref. Specification Section-8001, 8290)
E-104 | NS-14 | Supply, Installation of 1-to-12 Ports TV Cable Splitter | No. | 1 |  | 0
E-105 | NS-15 | Supply and Fixing of electric False Ceiling Fan Decorative 18″ 2×2, single phase and blade complete , including remote/ control and all accessories. | No. | 50 |  | 0
GREEN ENERGY METER & CONTROL EQUIPMENT
E-106 | NS-16 | Supply and Erection of Green Meter including Certification Regulations or Related NEPRA and PESCO Fee for installation and Activation of Green Energy Meter include Grid Flow Study from approved consultant of PESCO | Job | 1 |  | 0
E-107 | NS-17 | Providing Fixing of water Proof Type DC Distribution box MCB/FUSES for Each Strings (for each Inverter) including DC Breakers SPD with Terminals Complete in all respects | Job | 1 |  | 0
E-108 | NS-18 | Providing and Fixing of Weather station includes Wind Speed humidity,Ambbient temperature module Temperature control cable complete in all respect | Job | 1 |  | 0
E-109 | NS-19 | Providing and Fixing of Monitoring and Communication OEM Logger (4G Dongle) | Job | 1 |  | 0
E-110 | NS-20 | Providing and Fixing of cool only TYPE 1.5 ton Wall Mounted split inverter AC along with copper piping, with all accessories. Complete in all respect or as approved by the Engineer | Job | 2 |  | 0
Cost of Non-Scheduled Items (Rs.) | [5 empty] | 0
Total Cost of Scheduled Items & Non-Scheduled Items (Rs.) | [5 empty] | 0