## Summary
UNHCR PAKISTAN
CONSTRUCTION OF VOCATIONAL TRAINING INSTITUTE FOR WOMEN BUFFER ZONE, KARACHI
SUMMARY
ENGINEER'S ESTIMATE
S.No | DESCRIPTION | TOTAL AMOUNT (Rs.)
1 | Civil Works
2 | Electrical Works including Solarization
3 | Plumbing Works
4 | Natural Gas Works
Total (1 to 4) (Rs.) =

## 1. Civil
UNHCR PAKISTAN
CONSTRUCTION OF VOCATIONAL TRAINING INSTITUTE FOR WOMEN BUFFER ZONE, KARACHI
ENGINEER'S ESTIMATE
CIVIL WORKS
ITEM No. | PAK PWD SCHEDULE 2022 REF No./NS | DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) | (e) | (f) | (g)
GENERAL NOTE.
SCOPE : (Applicable to all sections)
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per specifications and as approved by the Engineer.
A1. |  | BUILDING CIVIL WORKS
SCHEDULED ITEMS
1 | (103-1) | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | %Cft | 33580
2 | (104-1) | Filling excavated earth available at site in foundation, plinth or under floor, etc. including breaking clods, dressing, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction complete within a lead of one chain (30.5 R.m) and lift of 5 feet (1.52m). | %Cft | 24210
3 | (104-9) | Supplying stacking and filling sand of approved quality from outside sources in foundation, trenches, plinth or under floor, etc. including dressing, watering and consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction and lift upto 5 feet (1 .52 m).Cooking Lab & Toilets) | %Cft | 670
4 | (105-14) + (105-27) | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using crushed graded boulders 1 inch (25 mm) and down gauge in foundation including leveling, compacting and curing etc.complete. | %Cft | 2010
5 | (108-11) | Providing damp proof course on vertical surface with 3/4 inch (19 mm) thick cement plaster 1:4 mixed with any approved water proofing agent including curing etc. complete, but excluding the cost of water proofing agent. | %Sft | 220
6 | (108-12) | Providing 4 coat of bitumen emulsion at 10 Lbs. per % sft. (0.49 Kg/sm) on walls and floor in ground floor. | %Sft | 76120
7 | (108-29) | Providing and laying double layer of polythene sheet of 500 gauge (0.005 or 0.13 mm thick) under floors for water proofing laid as per specifications and instructions of the Engineer-in-Charge. | %Sft | 12660
8 | (109-62) + (109-75) + (109-123) | Providing and laying in situ 1:2:4 (1 cement 2 sand and 4 coarse aggregate) cement concrete using screened graded bajri 3/4 inch (19 mm) and down gauge in any shape in superstructure including compacting, curing, cost of form work and its removal etc. complete in ground floor.(1st Floor Solar Pedestal & Roof treatment) | %Cft | 2690
| (109-62) +(109-75) +(109-76) +(109-123) | Second Floor | %Cft | 30
9 | (109-113) + (109-120) | Providing and laying 1:3:6 (1 cement 3 sand and 6 coarse aggregate) cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge in steps including cost of form work and its removal etc. complete in ground floor. | %Cft | 1380
10 | (110-02) + (110-93) | Providing and laying 1:3:6 cement concrete solid block masonry more than 6 inches (152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 in foundation, basement and plinth including scaffolding, raking out Joints and curing etc. complete; foundation and basement masonry upto 5 feet (1.52 Ru.m.) depth and plinth upto 4 feet (1.2 Ru.m.) height from ground level . | %Cft | 450
11 | (110-34) + (110-94) | Providing and laying 1:3:6 cement concrete solid block masonry more than 6 inches (152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | %Cft | 2580
| (110-34) +(110-70) +(110-94) | First Floor | %Cft | 2410
| (110-34) + (110-70) + (110-71) + (110-94) | Second Floor | %Cft | 370
12 | (110-44) + (110-94) | Providing and laying 1:3:6 cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | %Cft | 3840
| (110-44) + (110-70) + (110-94) | First Floor | %Cft | 3030
| (110-44) + (110-70) + (110-71) + (110-94) | Second Floor | %Cft | 45
13 | (114-1) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in column footing of required shape including form work and its removal, compacting, leveling and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | %Cft | 12530
14 | (114-4) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in foundation basement and plinth . | %Cft | 1800
15 | (114-8) + (114-134) + (114-137) + (114-146) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, Lawrencepur sand having a minimum works cube crushing strength of 3750 Ibs per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | %Cft | 2820
16 | (114-24) + (114-134) + (114-137) + (114-161) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. but excluding the cost of reinforcement, in ground floor. | %Cft | 3460
| (114-24) + (114-134) + (114-137) + (114-92) + (114-161) | First Floor | %Cft | 3330
| (114-24) + (114-134) + (114-137) + (114-92) + (114-93) + (114-161) | Second Floor | %Cft | 230
17 | (114-32) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight walls, vertical fins etc.3 inches (127 mm) to 5 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in Grond floor. | %Cft | 70
| (114-31) + (114-134) + (114-137) + (114-92) + (114-162) | First Floor | %Cft | 1010
| (114-31) + (114-134) + (114-137) + (114-92) + (114-93) + (114-162) | Second Floor | %Cft | 145
18 | (114-38) + (114-134) + (114-137) + (114-163) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight beams, lintels cantilever beams of required shape or section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | %Cft | 3960
| (114-38) + (114-134) + (114-137) + (114-92) + (114-163) | First Floor | %Cft | 6590
| (114-38) + (114-134) + (114-137) + (114-92) + (114-93) + (114-163) | Second Floor | %Cft | 200
19 | (114-50) + (114-134) + (114-137) + (114-163) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight stairs and landing of required section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | %Cft | 1690
| (114-50) + (114-134) + (114-137) + (114-92) + (114-163) | First Floor | %Cft | 1570
20 | (114-55) + (114-134) + (114-137) + (114-92) + (114-164) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in ordinary slab 3 inches (76 mm) to less than 5 inches (127 mm) thick including M.S Plates form work and M.S pipe folding and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor in first floor. | %Cft | 1120
21 | (114-56) + (114-134) + (114-137) + (114-164) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in ordinary slab 5 inches to 6 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | %Cft | 4070
| (114-56) + (114-134) + (114-137) + (114-92) + (114-164) | First Floor | %Cft | 3960
| (114-56) + (114-134) + (114-137) + (114-92) + (114-93) + (114-164) | Second Floor | %Cft | 185
22 | (114-57) + (114-134) + (114-137) + (114-164) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in ordinary slab more than 6 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in Ground Floor | %Cft | 540
| (114-57) + (114-134) + (114-137) + (114-92) + (114-164) | First Floor | %Cft | 670
23 | (114-55) + (114-136) | Providing and laying reinforced cement concrete using screened graded bajri 3/4 inch (19 mm) and down gauge having a minimum works cube crushing strength of 2250 Ibs. per sq inch (15.52 N/mm2) at 28 days with a mix not leaner than 1:2:4 in ordinary slab 3 inches (76 mm) to less than 5" (127 mm) thick including form work and its removal compacting and curing etc, complete but excluding the cost of reinforcement, in basement plinth and ground floor.(Cabinets & Vainty) | %Cft | 60
| (114-55) + (114-92) + (114-136) | First Floor | %Cft | 50
24 | (114-166) | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | Kg | 94800
| (114-166) + (114-174) | First Floor | Kg | 60700
| (114-166) + (114-174) + (114-175) | Second Floor | Kg | 2270
25 | (114-167) | Providing and laying ribbed deformed steel reinforcement bars with guaranteed minimum yield stress of 40,000 psi with and including the cost of straightening, cutting, bending, binding, wastage, complete in all kinds of RCC work . | Kg | 38780
| (114-167) + (114-174) | First Floor | Kg | 36630
| (114-167) + (114-174) + (114-175) | Second Floor | Kg | 1000
26 | (116-37) + (116-55) | Providing and laying 1st class burnt clay tiles of 9" X 4-1/2" X 1-1/2" size grouted with 1:3 cement mortar over 4" thick (avg) puddled earth compacted and smooth finished to slope mixed with bhoosa at the rate of one seer of bhoosa for one cft. of puddled earth in ground floor including flush pointing on tiles works with 1:3 cement mortar and curing complete. in First Floor | %Sft | 12660
27 | (117-2) | Providing and laying 1:4:8 cement concrete bed under floor using graded stone ballast 2" and down gauge with leveling and ramming, ramming, watering and curing etc. complete in ground floor. | %Cft | 4950
28 | (117-10) | Providing and laying terrazzo floor 1-1/4 inches (32 mm) thick consisting of 1/4 inch (6.4 mm) thicktopping 1:2 (one grey cement 2 approved marble chip No. 0 to 2) in ground floor over base of 1:2:4 (one cement 2 sand and 4 screened graded bajri) cement concrete 1 inch (25 m) thick laid in panels or pattern including form work, curing cutting, rubbing and polishing etc. complete.(Lecture Theatre) | %Sft | 3700
| (117-10) + (117-26) | First Floor | %Sft | 1380
29 | (117-46) + (117-77) | Providing and laying stairs / steps (in treads, rises ,mid stair landing & external side) floor of 3/4 inch (19 mm) thick Granite tiles Pakistani origin more than 3 Sq.ft. upto 5 Sq.ft- (more than 0.28 Sq.m upto 0.46 Sq.m) size fine dressed on the surface, without winding in ground floor over 1 inch (25 mm) cement mortar 1:2 setting the marble tiles with grey cement slurry over lime mortar, jointing and washing the tiles with white cement slurry including curing, rubbing and polishing etc. complete including the cost of mortar. | %Sft. | 1520
| (117-46) + (117-77) + (117-79) | First Floor | %Sft. | 1230
30 | (117-58) + (117-77) | Providing and laying stairs / steps (in treads, rises and mid stair landing) floor of 1 inch (25 mm) thick white marble tiles more than 3 Sq.ft. upto 5 Sq.ft- (more than 0.28 Sq.m upto 0.46 Sq.m) size fine dressed on the surface, without winding in ground floor over 1 inch (25 mm) cement mortar 1:2 setting the marble tiles with grey cement slurry over lime mortar, jointing and washing the tiles with white cement slurry including curing, rubbing and polishing etc. complete including the cost of mortar. | %Sft. | 1405
| (117-58) + (117-77) + (117-79) | First Floor | %Sft. | 410
31 | (117-75) | Extra for making nosing of treads as per design and instructions of the Engineer-in-Charge .. | Rft | 600
32 | (117-117) | Proving and laying floor 1 inch (25 mm) thick of cement tiles 12" X 12" X 1" (1/2 inch toping 1/2 inch base) or 305 mm X 305 mm X 25 mm (13 mm topping 12 mm base) in grey cement with pigment of dark shade in ground floor over 1 inch (25 mm) lime mortar 1:2 (one lime two sand) including setting the tiles with grey cement slurry over lime mortar, jointing and washing the tiles with grey cement slurry including grinding, rubbing, polishing and curing etc. complete including the cost of mortar . | %Sft. | 3000
33 | (117-172) | Providing and fixing wooden flooring in best quality imported teak wood planks 3/4 inch (19 mm) thick rebated including fixing with brass screws on deodar wood battens 1-1/2 inches X 2 inches (38 mm X 51 mm) placed at 12 inches (305 mm) centre to centre and filling the gap between planks and concrete base with bitumen and sand mixed in the ratio 9 Ibs. (4.1 Kg) of bitumen to one cft, (0.028 cum) of sand etc. complete in any floor.. | Sft. | 300
34 | (117-186) | Providing & laying light/colour unglazed vitrified porcelain tiles (polished) not exceeding 1600 Sq. cm and upto 3600 Sqcm each on walls & floors foreign make (Italian or equivalent except China make) in any floor laid with dry bond (stile bond) over on 1" thick cement mortar (1:3) including jointing the tiles with joint filler of approved qualityas per direction of the Engineer incharge. | %Sft. | 23590
35 | (119-06) | Providing and fixing double leaf steel doors made to crittal or equivalent standard and of approved sections fully panelled with M. S. Sheet of 16 gauge painted with two coats of red oxide paint including using approved brass section oxidized fitting iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | Sft | 35
36 | (119-61) | Providing and fixing fully glazed Bronze anodized or Powder Coated aluminum fixed windows partition as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), Deluxe model box section 101.76mm x 44.5mm and 2mm thick including the cost of aluminum, fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | Sft | 1160
37 | (119-88) | Providing and fixing fully glazed Bronz anodized or Powder Coated aluminium Swing door with frame as per British standard manufactured by Lucky,Alcop, Krudson, Pakistan cable and A.C.P. (fixing through their approved fabricators), Deluxe model section, 76.2mm x 38.1mm and 2mm thick including the aluminium fittings, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | Sft | 749
38 | (119-97) | Providing and fixing fully glazed Bronze anodized or Powder Coated aluminum Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), prime model box section 101mm x 30mm and 2mm thick including the cost of aluminum netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | Sft | 2365
39 | (119-121) | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | Sft | 4275
40 | (120-63) | Providing and fixing 1-1/2 inches (38 mm) thick solid core deodar wood flushed veneered door shutters, with and including the cost of commercial plywood facing 3 mm. thick (3 ply) on both faces, fixed over best quality deodar wood frame 2 inches wide alround 6 inches wide lock rail and 2nd class deodar wood solid core, i/c., 1/4 inch thick best quality deodar wood lipping on al! sides as per approved drawing, manufactured under power driven hydraulic press, including the cost of approved iron fittings but excluding the cost of handles and locking arrangement. | Sft | 783
41 | (121-70) | Providing and fixing with brass screws or specially supplied screws hydraulic door closer Rayobi or approved design No. 72, Japan make, cutting wood etc., to required shape and size as per direction of engineer-in-charge . | Each | 39
42 | (121-84) | Providing and fixing with brass screws door Alpha lock with handle of approved design (Taiwian make), cutting wood etc., to required shape and size with two operating keys as per direction of the Engineer-in-Charge. | Each | 26
43 | (122-2) | 1/4" thick cement plaster 1:4 on soffits of ceiling cantilever slabs sides and soffits of beams etc. in basement mezzanine and ground floor including making edges corners and curing etc. complete. | %Sft | 2760
| (122-2) + (122-87) | First Floor | %Sft | 12490
| (122-2) + (122-87) + (122-90) | Second Floor | %Sft | 330
44 | (122-4) | 1/2" (13 mm) thick cement plaster 1:4 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, corners, and curing etc., complete . | %Sft | 31670
| (122-4) + (122-87) | First Floor | %Sft | 28290
| (122-4) + (122-87) + (122-90) | Second Floor | %Sft | 7760
45 | (122-161) | Painting with Robbialac supper gloss synthetic (matt) enamel paint of approved make and shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | %Sft | 2500
46 | (122-162) | Painting with (ICI) Dulux Plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor. | %Sft | 59790
47 | (122-172) | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | %Sft | 21020
48 | (122-189) | Applying French or spirit polishing, two coat of approved make on wood work at any height in any floor . | %Sft | 1650
49 | (124-170) | Providing and laying 3/8"(9mm) thick Marble patties (Panel strips) upto 1" depth in floor and dado of any description in all floors. | Rft. | 2100
50 | (124-185) | Providing and fixing Dampa ceiling aluminum, China make 2' x 2' tiles/ strip ceiling including all accessories i.e,plump, rod etc complete as required in any floor. | Sft. | 1670
51 | (124-187) | Providing and fixing mineral fiber tiles 2' x 2' x 3/4" ceiling including T & L angle hanger clips jointing clips and G.I Wire etc complete as required in any floor. | Sft | 15230
52 | (124-192) | P/F kitchen cabinet wall mounted of 3/4" thick laminated board with best quality deodar wood frame and beading 1/8" thick hard board backing required section in approved pattern etc fixed on wall with rawal pugs,screws i/c the cost of gule , nails,screws, piano hinges, handles and painting or polishing etc as drawing complete all as respects. | Sft. | 240
53 | (124-193) | P/F kitchen cabinet floor mounted of 3/4" thick laminated board with best quality deodar wood frame and beading required section in approved pattern etc fixed on floor with rawal pugs,screws i/c the cost of gule , nails,screws, piano hinges, handles and painting or polishing etc as drawing complete all as respects. | Sft. | 270
54 | (124-199) | Providing and carrying out Termite proofing in foundations, under floors and wood work surface with a solution using of control TC with water and spraying the solution of the area to be treated as completed as per direction of Engineer Incharge. | Sft. | 14850
55 | (124-202) | Providing & fixing 2" dia stainless steel pipe (18 gauge) railing along with 4 Nos 3/4 dia paralled pipe having S/S pipe vertical post 2" dia at 3 ft C/C average spacing and 4" dia vertical post at start turing and end point including cost of labour, welding charges fitting & fixing in marble floor and wall etc complete the as per direction of the Engineer Incharge. | Rft. | 260
56 | (127-30) | Supplying and laying machine crushed 2" to 1/2" (51 mm to 13 mm) stone ballast of approved grade and quality in sub-base or base courses in required grade and camber and compacting to the required density by approved mechanical means (Vibratory Roller, Road Packer and Smooth Wheel Roller etc.) including watering with all lead and lift complete (actual compacted depth shall be considered for payment) | %Cft | 4750
57 | (134-2) | Cartage of sand, bajri, lime, surkhi, murum, manure, earth, building rubbish including loading, unloading and stacking etc. at site:
|  | 1 miles (1.6 km) lead. | %Cft | 4320
|  | 3 miles (4.8 km) lead. | %Cft | 6480
A2. |  | GUARD ROOM & GATE CIVIL WORKS
58 | (103-1) | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | %Cft | 1090
59 | (104-1) | Filling excavated earth available at site in foundation, plinth or under floor, etc. including breaking clods, dressing, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction complete within a lead of one chain (30.5 R.m) and lift of 5 feet (1.52m). | %Cft | 200
60 | (104-9) | Supplying stacking and filling sand of approved quality from outside sources in foundation, trenches, plinth or under floor, etc. including dressing, watering and consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction and lift upto 5 feet (1 .52 m).Toilet | %Cft | 20
61 | (105-14) + (105-27) | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using crushed graded boulders 1 inch (25 mm) and down gauge in foundation including leveling, compacting and curing etc.complete. | %Cft | 80
62 | (108-12) | Providing 4 coat of bitumen emulsion at 10 Lbs. per % sft. (0.49 Kg/sm) on walls and floor in ground floor. | %Sft | 2680
63 | (108-29) | Providing and laying double layer of polythene sheet of 500 gauge (0.005 or 0.13 mm thick) under floors for water proofing laid as per specifications and instructions of the Engineer-in-Charge. | %Sft | 170
64 | (109-113) + (109-120) | Providing and laying 1:3:6 (1 cement 3 sand and 6 coarse aggregate) cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge in steps including cost of form work and its removal etc. complete in ground floor. | %Cft | 25
65 | (109-62) + (109-123) | Providing and laying in situ 1:2:4 (1 cement 2 sand and 4 coarse aggregate) cement concrete using screened graded bajri 3/4 inch (19 mm) and down gauge in any shape in superstructure including compacting, curing, cost of form work and its removal etc. complete in ground floor.(Roof treatment) | %Cft | 40
66 | (110-34) + (110-94) | Providing and laying 1:3:6 cement concrete solid block masonry more than 6 inches (152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | %Cft | 300
67 | (110-44) + (110-94) | Providing and laying 1:3:6 cement concrete solid block masonry 4 to 6 inches (102 mm to 152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | %Cft | 50
68 | (114-1) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in column footing of required shape including form work and its removal, compacting, leveling and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | %Cft | 260
69 | (114-4) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in foundation basement and plinth . | %Cft | 55
70 | (114-8) + (114-134) + (114-137) + (114-146) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, Lawrencepur sand having a minimum works cube crushing strength of 3750 Ibs per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | %Cft | 85
71 | (114-24) + (114-134) + (114-137) + (114-161) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. but excluding the cost of reinforcement, in ground floor. | %Cft | 110
72 | (114-31) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight walls, vertical fins etc.4 inches (127 mm) to 6 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in Grond floor. | %Cft | 20
73 | (114-38) + (114-134) + (114-137) + (114-163) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight beams, lintels cantilever beams of required shape or section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | %Cft | 65
74 | (114-56) + (114-134) + (114-137) + (114-164) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in ordinary slab 5 inches to 6 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | %Cft | 80
75 | (114-166) | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | Kg | 2280
76 | (114-167) | Providing and laying ribbed deformed steel reinforcement bars with guaranteed minimum yield stress of 40,000 psi with and including the cost of straightening, cutting, bending, binding, wastage, complete in all kinds of RCC work . | Kg | 640
77 | (116-37) + (116-55) | Providing and laying 1st class burnt clay tiles of 9" X 4-1/2" X 1-1/2" size grouted with 1:3 cement mortar over 4" thick (avg) puddled earth compacted and smooth finished to slope mixed with bhoosa at the rate of one seer of bhoosa for one cft. of puddled earth in ground floor including flush pointing on tiles works with 1:3 cement mortar and curing complete. in First Floor | %Sft | 170
78 | (117-2) | Providing and laying 1:4:8 cement concrete bed under floor using graded stone ballast 2" and down gauge with leveling and ramming, ramming, watering and curing etc. complete in ground floor. | %Cft | 105
79 | (117-58) + (117-77) | Providing and laying stairs / steps (in treads, rises and mid stair landing) floor of 1 inch (25 mm) thick white marble tiles more than 3 Sq.ft. upto 5 Sq.ft- (more than 0.28 Sq.m upto 0.46 Sq.m) size fine dressed on the surface, without winding in ground floor over 1 inch (25 mm) cement mortar 1:2 setting the marble tiles with grey cement slurry over lime mortar, jointing and washing the tiles with white cement slurry including curing, rubbing and polishing etc. complete including the cost of mortar. | %Sft. | 30
80 | (117-75) | Extra for making nosing of treads as per design and instructions of the Engineer-in-Charge .. | Rft | 20
81 | (117-117) | Proving and laying floor 1 inch (25 mm) thick of cement tiles 12" X 12" X 1" (1/2 inch toping 1/2 inch base) or 305 mm X 305 mm X 25 mm (13 mm topping 12 mm base) in grey cement with pigment of dark shade in ground floor over 1 inch (25 mm) lime mortar 1:2 (one lime two sand) including setting the tiles with grey cement slurry over lime mortar, jointing and washing the tiles with grey cement slurry including grinding, rubbing, polishing and curing etc. complete including the cost of mortar . | %Sft. | 170
82 | (117-186) | Providing & laying light/colour unglazed vitrified porcelain tiles (polished) not exceeding 1600 Sq. cm and upto 3600 Sqcm each on walls & floors foreign make (Italian or equivalent except China make) in any floor laid with dry bond (stile bond) over on 1" thick cement mortar (1:3) including jointing the tiles with joint filler of approved qualityas per direction of the Engineer incharge. | %Sft. | 250
83 | (119-05) | Providing and fixing single leaf steel doors made to crittal or equivalent standard and of approved sections fully panelled with M. S. Sheet of 16 gauge painted with two coats of red oxide paint including using approved brass section oxidized fitting iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | Sft | 42
84 | (119-97) | Providing and fixing fully glazed Bronze anodized or Powder Coated aluminum Sliding windows as per British standard manufactured by Lucky, Alcop, Krudson, Pakistan Cables and A.C.P. (fixing through their approved fabricators), prime model box section 101mm x 30mm and 2mm thick including the cost of aluminum netting ,fitting, with all accessories cutting hole etc. and making good damages to walls etc. complete as required in any floor as per direction of engineer-in-charge, but excluding the cost of glass pans. | Sft | 20
85 | (119-121) | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | Sft | 20
86 | (121-84) | Providing and fixing with brass screws door Alpha lock with handle of approved design (Taiwian make), cutting wood etc., to required shape and size with two operating keys as per direction of the Engineer-in-Charge. | Each | 2
87 | (122-2) | 1/4" thick cement plaster 1:4 on soffits of ceiling cantilever slabs sides and soffits of beams etc. in basement mezzanine and ground floor including making edges corners and curing etc. complete. | %Sft | 160
88 | (122-4) | 1/2" (13 mm) thick cement plaster 1:4 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, corners, and curing etc., complete . | %Sft | 1600
89 | (122-161) | Painting with Robbialac supper gloss synthetic (matt) enamel paint of approved make and shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor . | %Sft | 75
90 | (122-162) | Painting with (ICI) Dulux Plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor. | %Sft | 560
91 | (122-172) | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | %Sft | 1160
92 | (124-199) | Providing and carrying out Termite proofing in foundations, under floors and wood work surface with a solution using of control TC with water and spraying the solution of the area to be treated as completed as per direction of Engineer Incharge. | Sft. | 170
93 | (127-30) | Supplying and laying machine crushed 2" to 1/2" (51 mm to 13 mm) stone ballast of approved grade and quality in sub-base or base courses in required grade and camber and compacting to the required density by approved mechanical means (Vibratory Roller, Road Packer and Smooth Wheel Roller etc.) including watering with all lead and lift complete (actual compacted depth shall be considered for payment) | %Cft | 90
94 | (134-2) | Cartage of sand, bajri, lime, surkhi, murum, manure, earth, building rubbish including loading, unloading and stacking etc. at site:
|  | 1 miles (1.6 km) lead. | %Cft | 1500
A3. |  | BOUNDARY WALL
95 | (103-1) | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | %Cft | 9900
96 | (105-14) + (105-27) | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using crushed graded boulders 1 inch (25 mm) and down gauge in foundation including leveling, compacting and curing etc.complete. | %Cft | 900
97 | (108-12) | Providing 4 coat of bitumen emulsion at 10 Lbs. per % sft. (0.49 Kg/sm) on walls and floor in ground floor. | %Sft | 24840
98 | (110-34) + (110-94) | Providing and laying 1:3:6 cement concrete solid block masonry more than 6 inches (152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | %Cft | 4050
99 | (114-1) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in column footing of required shape including form work and its removal, compacting, leveling and curing etc. complete but excluding the cost of reinforcement, in foundation basement and plinth | %Cft | 1890
100 | (114-4) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in foundation basement and plinth . | %Cft | 540
101 | (114-8) + (114-134) + (114-137) + (114-146) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, Lawrencepur sand having a minimum works cube crushing strength of 3750 Ibs per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in plinth beams of required shape and design including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, tn foundation basement and plinth | %Cft | 990
102 | (114-24) + (114-134) + (114-137) + (114-161) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. but excluding the cost of reinforcement, in ground floor. | %Cft | 1080
103 | (114-38) + (114-134) + (114-137) + (114-163) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight beams, lintels cantilever beams of required shape or section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | %Cft | 1080
104 | (114-166) | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | Kg | 22070
105 | (114-167) | Providing and laying ribbed deformed steel reinforcement bars with guaranteed minimum yield stress of 40,000 psi with and including the cost of straightening, cutting, bending, binding, wastage, complete in all kinds of RCC work . | Kg | 6700
106 | (119-38) | Providing M. S. tees, angles and flats including fixing in position etc. complete in ground floor. | Kg | 615
107 | (122-08) + (122-37) | 3/4" (19 mm) thick cement plaster 1:4 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, corners, and curing etc.complete.(With Grooves) | %Sft | 20610
108 | (122-172) | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | %Sft | 20610
109 | (124-203) | Providing and fixing G.I Razor wire 18 gauge 1'-6" at 6" center to center with double razor and 1/4 inch dia G.I wire bars at top and bottom etc complete as per direction of the Engineer incharge. | P.Kg | 180
110 | (134-2) | Cartage of sand, bajri, lime, surkhi, murum, manure, earth, building rubbish including loading, unloading and stacking etc. at site:
|  | 1 miles (1.6 km) lead. | %Cft | 7425
A4. |  | UNDER GROUND WATER TANK,MANHOLE,VALVE CHAMBER & DRAIN
111 | (103-10) | Excavation for raft foundations, underground tanks and septic tanks (rectangular or square) in all kinds of soil (except gravelly and murum soil wet silt, clay or mud, conglomeration of gravel and boulders, soft, sandy or disintegrated and hard rock) and back filling the excavated material all round the trenches including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead up to one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | %Cft | 9820
| (103-28) | 5'-00" to 8'-00" Depth | %Cft | 4620
| (103-28) | 8'-00" to 11'-00" Depth | %Cft | 4430
| (103-28) | 11'-00" to 14'-00" Depth | %Cft | 2280
| (103-28) | 14'-00" to 17'-00" Depth | %Cft | 160
| (103-28) | 17'-00" to 20'-00" Depth | %Cft | 140
112 | (104-1) | Filling excavated earth available at site in foundation, plinth or under floor, etc. including breaking clods, dressing, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction complete within a lead of one chain (30.5 R.m) and lift of 5 feet (1.52m). | %Cft | 850 |  |  |  |  | #REF! | #REF!
113 | (105-14) + (105-27) | Providing and laying 1:4:8 (1 cement 4 sand and 8 coarse aggregate) cement concrete using crushed graded boulders 1 inch (25 mm) and down gauge in foundation including leveling, compacting and curing etc.complete. | %Cft | 600
114 | (106-12) | Providing and laying in situ 1:3:6 (1 cement 3 sand and 6 coarse aggregate) cement concrete using crushed graded boulders 3/4 inch (19 mm) and down gauge in foundation, basement and plinth including form work ,compacting, curing and its removal of form work etc., complete, foundation and basement up to 5 feet (1.52 m) depth and plinth up to 4 feet (1.2 m) height from ground level.(Benching) | %Cft | 120
115 | (108-12) | Providing 4 coat of bitumen emulsion at 10 Lbs. per % sft. (0.49 Kg/sm) on walls and floor in ground floor. | %Sft | 16520 | [8 empty] | #REF!
116 | (109-113) + (109-120) | Providing and laying 1:3:6 (1 cement 3 sand and 6 coarse aggregate) cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge in steps including cost of form work and its removal etc. complete in ground floor. | %Cft | 40
117 | (110-34) + (110-94) | Providing and laying 1:3:6 cement concrete solid block masonry more than 6 inches (152 mm) thick using graded screened bajri 3/4 inch (19 mm) and down gauge set in cement mortar 1:5 including scaffolding, raking out joints and curing etc. complete in ground floor superstructure. | %Cft | 330
118 | (114-4) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including form work and its removal, compacting and curing etc. but excluding the cost of reinforcement, in foundation basement and plinth . | %Cft | 105
119 | (114-24) + (114-134) + (114-137) + (114-161) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in columns of square or rectangular shape of regular section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. but excluding the cost of reinforcement, in ground floor. | %Cft | 80
120 | (114-24) + (114-134) + (114-137) + (114-92) + (114-161) | First Floor | %Cft | 20
121 | (114-32) + (114-134) + (114-137) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight walls, vertical fins etc.3 inches (127 mm) to 5 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in Grond floor. | %Cft | 40
122 | (114-38) + (114-134) + (114-137) + (114-163) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight beams, lintels cantilever beams of required shape or section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement and ground floor. | %Cft | 140
123 | (114-50) + (114-134) + (114-137) + (114-163) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in straight stairs and landing of required section including M.S Plates form work and M.S pipe folding and its removal, compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | %Cft | 110
124 | (114-56) + (114-134) + (114-137) + (114-164) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in ordinary slab 5 inches to 6 inches (152 mm) thick including M.S Plates form work and M.S pipe folding and its removal compacting and curing etc. complete but excluding the cost of reinforcement, in basement plinth and ground floor. | %Cft | 145
125 | (114-99) + (114-134) + (114-137) + (114-162) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in foundation or bottom slab of rectangular underground tank including (M.S Plates) form works and its removal, levelling, compacting and curing etc. complete but excluding the cost of reinforcement. | %Cft | 2150
126 | (114-101) + (114-134) + (114-137) + (114-162) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in walls of rectangular underground water tank including (M.S Plates) form works and its removal, compacting and curing etc. complete, but excluding the cost of reinforcement. | %Cft | 1970
127 | (114-104) + (114-134) + (114-137) + (114-162) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, Lawrencepur sand having a minimum works cube crushing strength of 3750 Ibs. per sq inch at 28 days with a mix not leaner than 1:1-1/2:3 in top slab of rectangular underground water tank or septic tank including (M.S Plates) form works and its removal, compacting and curing etc. complete, but excluding the cost of reinforcement.. | %Cft | 765
128 | (114-99) + (114-136) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 2250 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in foundation or bottom slab of rectangular underground tank including form works and its removal, compacting and curing etc. complete, but excluding the cost of reinforcement.(Manhole & Drain) | %Cft | 335
129 | (114-101) + (114-136) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge,sand having a minimum works cube crushing strength of 2250 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in walls of rectangular underground water tank or septic tank including form works and its removal, compacting and curing etc. complete, but excluding the cost of reinforcement.(Manhole & Drain) | %Cft | 740 |  |  |  |  | 745
130 | (114-104) + (114-136) | Providing and laying reinforced cement concrete using crush graded boulders 3/4 inch (19 mm) and down gauge, sand having a minimum works cube crushing strength of 2250 Ibs. per sq inch at 28 days with a mix not leaner than 1:2:4 in top slab of rectangular underground water tank or septic tank its removal, compacting and curing ate. complete but excluding the cost of reinforcement.(Manhole & Drain) | %Cft | 80 |  |  |  |  | 1155 | 0.029729
131 | (114-166) | Providing and laying hard grade ribbed deformed (minimum yield point 60,000 psi) reinforcement bars with & including the cost of straightening, cutting, bending, binding, wastage, and such overlaps as are not shown in the drawings, placing in position on cement concrete 1:2:4 precast or m.s. chairs, tying with binding wire, cost of chairs and wires etc. in all kinds of RCC work in foundation, basement, plinth and ground floor of building including septic tanks and under ground tanks and in projections for future extension . | Kg | 13040 |  |  |  |  | 13.04
132 | (114-167) | Providing and laying ribbed deformed steel reinforcement bars with guaranteed minimum yield stress of 40,000 psi with and including the cost of straightening, cutting, bending, binding, wastage, complete in all kinds of RCC work . | Kg | 3980 |  |  |  |  | 3.98
133 | (117-2) | Providing and laying 1:4:8 cement concrete bed under floor using graded stone ballast 2" and down gauge with leveling and ramming, ramming, watering and curing etc. complete in ground floor. | %Cft | 190 |  |  |  |  | 1711.4651
134 | (117-6) + (114-136) | Providing, and laying floors of 2 inches (51 mm) thick 1:2:4 (1 cement 2 sand and 4 coarse aggregate) cement concrete using crush graded boulders 3/4 inches (19 mm) and down gauge in ground floor laid in panels including form work, consolidation, finishing, curing etc. complete. | %Sft | 610 |  |  |  |  | 128.125
135 | (117-117) | Proving and laying floor 1 inch (25 mm) thick of cement tiles 12" X 12" X 1" (1/2 inch toping 1/2 inch base) or 305 mm X 305 mm X 25 mm (13 mm topping 12 mm base) in grey cement with pigment of dark shade in ground floor over 1 inch (25 mm) lime mortar 1:2 (one lime two sand) including setting the tiles with grey cement slurry over lime mortar, jointing and washing the tiles with grey cement slurry including grinding, rubbing, polishing and curing etc. complete including the cost of mortar . | %Sft. | 500 |  |  |  |  | 1711.4651
136 | (118-2) | Providing and laying dado and skirting with 1/2 inch (13 mm) thick cement plaster 1:3 in ground floor including finishing smooth with a floating coat of neat cement, rounding corners and curing etc. complete.. | %Sft. | 250
137 | (119-06) | Providing and fixing double leaf steel doors made to crittal or equivalent standard and of approved sections fully panelled with M. S. Sheet of 16 gauge painted with two coats of red oxide paint including using approved brass section oxidized fitting iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor. | Sft | 28
138 | (119-37) | Providing rolled steel Joists and channels including hoisting and fixing in position in cement concrete in ground floor but excluding cost of cement concrete.(Steel Girder as shown in drawing) | Kg | 160 |  |  |  |  | 7.6992 | 0.3937 | 254 | 38.1
[9 empty] | 161.6827 |  | 127 | 0.1875 | 4.7625
139 | (119-47) | Providing & fixing single leaf hung steel Windows and ventilators made of M.S. pipe (18 gauge) of approved section comprising of frame L-section l-1/2" x l-l/2" shutter frame ofT-Section 2"xl" and l/2"xl/2" M.S. pipe beading for fixing glass panes, clamping the screws at 4 inches center to center, rubber packing for glazing, painted two coats with red oxide paint including using iron lugs, cutting holes and making good damages to walls etc. complete as required in any floor but excluding the cost of glass panes. | Sft | 48 |  |  |  |  | 0.81347
390.4663
140 | (119-51) | Providing and fixing square pipe railing size l-l/2" x l-l/2" of 16 gauge comprising vertically posts and horizontal bracing of M.S. square pipe of same size as per design including cost of cutting fitting including embedding the braces and posts in floor and walls and making good with cement concrete 1:2:4 in any floor.. | Rft | 45
141 | (119-121) | Providing and fixing Tinted glass panes 5mm thick to M.S. Box pipe / Aluminium doors, windows and ventilators etc including the cost of labour but excluding the cost of M.S. square pipe beading, rubber packing and screw in any floor at any height. | Sft | 48
142 | (122-2) | 1/4" thick cement plaster 1:4 on soffits of ceiling cantilever slabs sides and soffits of beams etc. in basement mezzanine and ground floor including making edges corners and curing etc. complete. | %Sft | 690
143 | (122-4) | 1/2" (13 mm) thick cement plaster 1:4 on walls and columns etc. in basement, plinth, mezzanine and ground floor including making edges, corners, and curing etc., complete . | %Sft | 3050
144 | (122-162) | Painting with (ICI) Dulux Plastic emulsion paint VIP of approved shade two coats over and including the cost of one priming coat complete over plastered surface at any height in any floor. | %Sft | 2480
145 | (122-172) | Painting three coats with weather shield paint deluxe (ICI) make of approved shade on plaster surface (External) and including the cost of cleaning the surface, sand papering etc. complete at any height in any floor. | %Sft | 1280
146 | (124-170) | Providing and laying 3/8"(9mm) thick Marble patties (Panel strips) upto 1" depth in floor and dado of any description in all floors. | Rft. | 320 |  |  |  |  | 314
147 | (124-97) | Providing and fixing PVC ribbed water stops 9" (229 mm) wide in vertical or horizontal expansion joints including cutting or jointing etc., complete in all floors. | Rft | 180
148 | (127-30) | Supplying and laying machine crushed 2" to 1/2" (51 mm to 13 mm) stone ballast of approved grade and quality in sub-base or base courses in required grade and camber and compacting to the required density by approved mechanical means (Vibratory Roller, Road Packer and Smooth Wheel Roller etc.) including watering with all lead and lift complete (actual compacted depth shall be considered for payment) | %Cft | 140
149 | (132-2) | Cartage of sand, bajri, lime, surkhi, murum, manure, earth, building rubbish including loading, unloading and stacking etc. at site:
|  | 1 miles (1.6 km) lead. | %Cft | 20600 |  |  | #REF! | 2900
COST OF SCHEDULED ITEM (Rs.) = | [5 empty] | 0
NON-SCHEDULED ITEMS
A5. |  | BUILDING WORKS
STRUCTURAL STEEL WORKS
Ref. Spec. No. 3000, 6700
150 | 1 | Providing and fixing in position 22 gauge expanded metal lath on areas as specified in joints etc. under plaster. | Sft. | 3500
151 | 2 | Supply and Fixing MS Sheet 16 guage(10'' x 2'') box type chowkats including fixing in position with all charges for Hold fast, Hinges and Painting etc. | Rft | 510
152 | 3 | 12mm-th. tempered Glass Partition wall as per approved manufacturer or as per approved manufactured including all fittings and fixtures as per approved shop drawings complete in all respect. | Sft. | 170
153 | 4 | Providing and fixing fiber roof of 5 ply fiber sheet and 2" x 2" M.S Box pipe 16 gauge main frame beams and centeal bracing 2" x 2" at 24" c/c diagonal and 2" x 2" support upto 2 feet c/c cutting fitting, welding painting etc, complete as par direction of engineer incharge. | Sft. | 1750
WATER PROOFING & PAINTING
Ref. Spec. No. 6411
154 | 5 | Providing and applying 2 coat of Sika seal 105 on floor, complete in all respects and as directed by the Engineer's Incharge. | Sft | 1670
155 | 6 | Water proofing treatment of roof slab comprising one layer of 2mm thick bituminous membrane over primer coated surface as per manufacturers specifications | Sft. | 12660
FLOOR & WALL FINISHES
Ref. Spec. No. 6531, 6600
156 | 7 | 1" thick (minimum) chemically pre-polished marble slabs on vanity and counter tops of premimum quality available in the market and as approved by the Engineer (of approved colour/shade/texture), with rounded edges, jointed and pointed in 1:2 cement sand mortar (white cement with imported colour pigments) and grouted with 1:3 cement sand grout and base, including cutting, etc, complete. | Sft. | 390
157 | 8 | Providing & fixing Carpet tile approved design /colour/shade/texture on floor fixed using approved adhesive complete in all respects.(Lecture Theatre) | Sft. | 3600
CARPENTRY, JOINERY
Ref. Spec. No. 4600, 6250, 6700
158 | 9 | Providing & fixing uPVC white color full body doors with UPVC frame and chowkat including, locks and all hardware fittings, etc. complete in all respects | Sft | 252
PLAIN AND REINFORCED CONCRETE
Ref. Spec. No. 2100, 2300
159 | 10 | Providing and laying reinforced cement concrete using concrete (1:3:6) in Stub columns on 2nd/3rd floor using O.P Cement, form work, curing etc. complete in all respects. | Cft. | 1110
A6. |  | GUARD ROOM & GATE CIVIL WORKS
STRUCTURAL STEEL WORKS
Ref. Spec. No. 3000, 6700
160 | 11 | Providing and fixing in position 22 gauge expanded metal lath on areas as specified in joints etc. under plaster. | Sft. | 160
161 | 12 | Provide & Fabricating and fixing in position steel gate & wicket gate as per design and details shown on drawing and approved by the engineer including cutting, welding, bending, fabricating, red oxide and enamel painting, rollers, rolling track, Locking arrangments etc. complete in all respects. (Gate) | Sft. | 180
WATER PROOFING & PAINTING
Ref. Spec. No. 6411
162 | 13 | Providing and applying 2 coat of Sika seal 105 on floor, complete in all respects and as directed by the Engineer's Incharge. | Sft | 20
163 | 14 | Water proofing treatment of roof slab comprising one layer of 2mm thick bituminous membrane over primer coated surface as per manufacturers specifications | Sft. | 170
A7. |  | BOUNDARY WALL
STRUCTURAL STEEL WORKS
Ref. Spec. No. 3000, 6700
164 | 15 | Providing and fixing in position 22 gauge expanded metal lath on areas as specified in joints etc. under plaster. | Sft. | 1545
A8. |  | UNDER GROUND WATER TANK, MANHOLE, VALVE CHAMBER & DRAIN
STRUCTURAL STEEL WORKS
Ref. Spec. No. 3000, 6700
165 | 16 | Providing and fixing in position 22 gauge expanded metal lath on areas as specified in joints etc. under plaster. | Sft. | 160
166 | 17 | Supply and installation of Mild steel grating cover with frame on drain including all fittings for complete installation of following clear widths.9" to 12" wide L1 11/2" x11/2"x1/4" thick L2 11/2" x11/2"x1/4 thick & 1/2" M/S bar @ 4" c/c. | Rft. | 285
COST OF NON-SCHEDULED ITEM (Rs.) = | [5 empty] | 0
TOTAL COST OF SCHEDULED & NON-SCHEDULED ITEM (Rs.) = | [5 empty] | 0

## 2. Electrical
UNHCR PAKISTAN
CONSTRUCTION OF VOCATIONAL TRAINING INSTITUTE FOR WOMEN BUFFER ZONE, KARACHI
ENGINEER'S ESTIMATE
ELECTRICAL WORKS
ITEM No. | PAK PWD SCHEDULE 2022 REF No./NS | DESCRIPTION | UNIT | QTY | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) | (b) | (c) | (d) | (e) | (f) | (g)
GENERAL NOTE.
SCOPE : (Applicable to all sections)
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per specifications and as approved by the Engineer.
B1. |  | BUILDING ELECTRICAL WORKS
SCHEDULED ITEMS
POINT WIRING IN RECESSED PVC CONDUIT
1 | 2-3-01 | Wiring for light or fan point with (3/.029") pvc insulated wire in 20 mm² (3/4") dia upvc conduit recessed in the wall , column , roof including 1 mm² single core pvc insulated wire as ECC as Required. | Point | 400
EXTENSION /ADDITIONAL POINT WIRING
2 | 2-7-03 | Extension /additional wiring for light fan call bell or light plug point controlled with same switch with (3/.029") pvc insulated wire in 20 mm (3/4") dia PVC conduit recessed in the wall , column or roof including 1mm² single core pvc insulated wire as ECC as required | P/Point | 120
SINGLE PVC INSULATED WIRE AND PVC CABLE IN EXISTING CONDUITS/DUCTS
3 | 2-26-17 | Supply & drawing of 400 mm², single core, PVC insulated wire in all kinds of existing or given conduit/cable duct as required. | Rft | 3000
4 | 2-26-06 | Supply & drawing of 16 mm², single core, PVC insulated wire in all kinds of existing or given conduit/cable duct as required. | Rft | 50
5 | 2-26-10 | Supply & drawing of 70 mm², single core, PVC insulated wire in all kinds of existing or given conduit/cable duct as required. | Rft | 200
6 | 2-26-08 | Supply & drawing of 35 mm², single core, PVC insulated wire in all kinds of existing or given conduit/cable duct as required. | Rft | 200
7 | 2-26-07 | Supply & drawing of 25 mm², single core, PVC insulated wire in all kinds of existing or given conduit/cable duct as required. | Rft | 1500
2 WIRE WITH ECC WIRE IN EXISTING CONDUITS/CABLE DUCT
8 | 2-27-02 | Supply & drawing of 2 x2.5 mm² single core pvc insulated wire including 1 mm² pvc insulated wire single core wire as ECC in all kind of existing or given conduits /cable duct as required | Rft | 3500
9 | 2-27-03 | Supply & drawing of 2 x4 mm² single core pvc insulated wire including 1.5 mm² pvc insulated wire single core wire as ECC in all kind of existing or given conduits /cable duct as required.(Db to first Socket , Socket to Socket) | Rft | 14000
UPVC CONDUIT & DUCT
10 | 2-61-05 | Supply and fixing 50mm (2") dia Upvc conduit with all especial such as bends, sockets, junction etc Fitted on surface as required | P/Rft | 250
11 | 2-61-06 | Supply and fixing 20mm (3/4") dia Upvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 10000
12 | 2-61-07 | Supply and fixing 25mm (1") dia pvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 6000
13 | 2-61-08 | Supply and fixing 30mm (1-1/4") dia pvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 300
SCHNEIDER /PHILIPS ACCESSORIES ON RESSED METAL BOARD
14 | 2-66-02 | Providing & fixing 10 Amps Polycarbonate flame retardant, Two way Switch with fancy required gang plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. | Each. | 6
15 | 2-66-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. | Each | 90
16 | 2-66-12 | Providing & fixing Polycarbonate flame retardant, tv socket with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. (Clipsal make) | Each | 15
ELECTRIC FANS
CEILING FAN
17 | 2-80-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, standard length of down rod including connection with 14.0076" flexible wire complete as required. (without regulator) Millat / Pak / Asia / Younas / Climax / Royal. | Each | 90
WALL BRACKET FAN
18 | 2-81-01 | Providing & installing 35 Cm (14") wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat / Pak / Asia / Younas / Climax / Royal. | Each | 20
FAN CLAMPS
19 | 2-87-06 | Providing & fixing 3"x4"x5" size (14 SWG) thick recessed type fan clamp box with 1/2" dia MS bar fan clamp fixed in roof at casting time as required. | Each. | 90
DOUBLE ACTION PLASTIC BODY EXHAUST FANS
20 | 2-85-02 | Providing & installing 25 Cm (10") sweep Double action Plastic body exhaust fan complete with blades, motor & regulator & pulling cord switch etc. fixed in existing hole including connection with 14 /.0076" flexible wire complete as required. Millat / Pak / Asia / Younas / Climax / Royal. | Each | 12
4 CORE LT UN ARMOURED CABLE IN EXISTING CONDUIT OR CABLE DUCT
21 | 3-4-01(a) | Providing & laying 4 core, 16 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , un armoured, L.T cable in existing all kind of conduit or cable duct as per Pak. P.W.D specification as required. | P/Rft | 40
22 | 3-4-01© | Providing & laying 4 core, 35 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , un armoured, L.T cable in existing all kind of conduit or cable duct as per Pak. P.W.D specification as required. | P/Rft | 40
23 | 3-4-01 d | Providing & laying 4 core, 50 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , un armoured, L.T cable in existing all kind of conduit or cable duct as per Pak. P.W.D specification as required. | P/Rft | 1500
`
24 | 3-4-01 e | Providing & laying 4 core, 70 mm², PVC insulated & PVC sheathed, 600/1000 volts grade with stranded copper conductor , un armoured, L.T cable in existing all kind of conduit or cable duct as per Pak. P.W.D specification as required. | P/Rft | 450
EARTHING AND LIGHTNING ARRESTOR
25 | 3-8-01 | Providing and fixing Earthing set with 2'x2'x1/8" copper plate Buried in the ground at the depth of 12 feet or less if water comes out from the ground level (with salt and charcoal or earthing chemical powder ) etc making the pit 12 feet deep by excavation of all type of soil (except soft or hard rock)i/c fixing of 8 SWG copper wire in 1/2" GI conduit complete in all respect as required. | Job | 10
26 | 3-8-04 | Providing and fixing 1'' diameter 3ft long lighting copper rod with five spikes and balls on its head as required. | Job | 2
27 | 3-8-07 | Providing and fixing 1-1/2'' x 1/3'' Thick copper strip with suitable saddle at 12'' intervals complete as required. | P/Rft | 700
ADDRESSABLE FIRE ALARM SYSTEM
28 | 7-1-02 | Providing and fixing , testing and commissioning of microprocessor based 02 loop analog addressable and 2 wire fire control panel surface /recessed mounted type with full switching programming capabilities system suitable operation of 230 volts 50 hz with full functionality as per specification of manufacturer allied component with T&P etc and as per specific drawing imported Approved make /model or as approved by the Engineer incharged as required. | Job | 1
29 | 7-1-06 | Providing and fixing , testing and commissioning of analog addressable inoization smoke detector with addressable base with full functionality switching programming capabilities system as per specification & recommendation of drawings / manufacturer allied component with T&P etc imported Approved make /model or as approved by the Engineer incharged as required. | Job | 70
30 | 7-1-07 | Providing and fixing , testing and commissioning of analog addressable inoization heat detector with addressable base with full functionality switching programming capabilities system as per specification & recommendation of drawings / manufacturer allied component with T&P etc imported Approved make /model or as approved by the Engineer incharged as required. | Job | 3
31 | 7-1-09 | Providing and fixing , testing and commissioning of analog addressable manual brake glass unit with addressable base with full functionality switching programming capabilities system as per specification & recommendation of drawings / manufacturer allied component with T&P etc imported Approved make /model or as approved by the Engineer incharged as required. | Job | 12
32 | 7-1-11 | Providing and fixing , testing and commissioning of analog addressable electronic sounder with Flasher addressable base with full functionality switching programming capabilities system as per specification & recommendation of drawings / manufacturer allied component with T&P etc imported Approved make /model or as approved by the Engineer incharged as required. | Job | 12
FIRE RESISTANT CABLE
33 | 7-03-01 | 2 x 1.5 sq.mm twin + earth fire resistant cable complying 3/4 inch dia pvc conduit complete in all respect. | Mtr | 2200
(SUNLIGHT , PIERE LIGHT , FUTURE TECHNOLOGY)
34 | 2-78-01(a) | Supply installation testing & commissioning of recessed / surface mounted Ceiling light/down light including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (7-10) Watts | Each | 25
35 | 2-78-01(c) | Supply installation testing & commissioning of recessed / surface mounted Ceiling light/down light including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (18-20) Watts | Each | 150
36 | 2-78-02(a) | Supply installation testing & commissioning of recessed / surface mounted led panel light including driver having war/ neutral white / cool white colour 80-100 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. 36 Watts (2ft x 2ft) | Each | 200
37 | 2-78-03(a) | Supply installation testing & commissioning of LED Tube / Batten Lights including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 10000-15000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (18-20) Watts 2 Feet | Each | 10
38 | 2-78-03(b) | Supply installation testing & commissioning of LED Tube / Batten Lights including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 10000-15000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (18-20) Watts 4 Feet | Each | 10
39 | 2-78-03(c) | Supply installation testing & commissioning of LED Tube / Batten Lights including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 10000-15000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (36) Watts 4 ft | Each | 5
40 | 2-78-05(c) | Supply installation testing & commissioning of LED Flood Lights including driver having war/ neutral white / cool white colour 110-120 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (80-110) Watts. | Each | 15
41 | 2-78-07 (c) | Supply installation testing & commissioning of LED Street Lights including driver having war/ neutral white / cool white colour 110-120 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (100-120) Watts. | Each | 20
INDOOR/ POLE MOUNTED TRANSFORMER
42 | 3-11-04 | Providing fixing and commissioning in door / pole mounted step down 11000/400 volts three phase 50 hz , transformer as per electricity code complete in all respect as required (400 KVA) | Each | 1
HT 11 KV CABLE
43 | 3-13-02 | Providing and laying HT 11 KV 3 Core 120 mm2 stranded copper conductor XLPE Insulated cu taped screened pvc bedded and Pvc sheated armoured cable laid in existing all kind of pipes cable duct channel etc as per pak P.W.D specification required. | P/Meter | 40
44 | 3-'14-01 © | Providing and fixing indoor/outdoor, 120 mm² to 185 mm², 3 core, 11KV, XLPE, heat shrink termination ends Kit complete in all respect as required | P/Job | 2
SPLIT AIR CONDITIONING SYSTEM (IMPORTED)
45 | 6-01-2(b) | Supply and installation of Split Wall Type Air Conditioner Kenwood, Gree, DAIKIN (Inverter) (heat & cool ) (1.5-1.6 )Ton including soft copper with foam insulation for split type air conditioner Complete in all respect as approved by the Engineer | Job. | 48
FLOOR STANDING AIR CONDITIONING SYSTEM (IMPORTED)
46 | 6-03-1(b) | Supply and installation of Floor Standing Type Air Conditioner (Heat & cool) Kenwood, Gree, DAIKIN (Inverter) 4 Ton including soft copper with foam insulation for air conditioner Complete in all respect as approved by the Engineer | Job. | 8
SOLAR SYSTEM (PHOTOVOLTAIC)
47 | 9-03-01 | Providing, Installation, testing & commissioning of mono crystalline A Grade Tier 1, High Efficiency, IEC Certified, Solar panel, including cabling, making connections, etc., complete in all respect as approved by the Engineer Incharge | P/Watt | 300000
IP CCTV SYSTEM
48 | 8-4-01 | Supply at site, installation, testing & commissioning of Bullet IP - Cameras, having following specifications: Image device at least 1/2.8 inch resolution & frames/sec : At least 2MP /30FPS Video compression H.265, H.264 MJPEG Focal length (varifocal): At least up to 12 mm, Min illumination: 0 lux (B/W) 0.095 lux colour, infrared viewable length: At least 30 m, weather proof standard: IP 66 at least Vandal Proof Standards: At Least IK 10, complete in all respects. as approved by the Engineer Incharge. | Job. | 30
49 | 8-4-02 | Supply at site, installation, testing & commissioning of Mini Dome IP - Cameras, having following specifications: Image device at least 1/2.8 inch resolution & frames/sec : At least 2MP /30FPS Video compression H.265 , H264 MJPEG Focal length (varifocal): At least up to 12 mm Min illumination: 0 lux (B/W) 0.095 lux colour infrared viewable length :At least 30 m weather proof standards IP 66 at least Vandal Proof Standards At Least IK 10 complete in all respects. as approved by the Engineer Incharge. | Job. | 12
CAT-6 CABLE
50 | 8-5-01 | Wiring of CCTV Camera with UTP Cat-6 in existing PVC Conduits/duct i/c connectors complete in all respect. | P/ Meter | 1600
51 | 8-6-04 | Supply, installation, testing & commissioning of 32-Channel NVR 32 POE /POE+ PORTS Having Following Specifications: Max Recording Rate 256 Mbps Embedded system Linus or Latest VGS and HDMI (upto 4k supports ) & Dual Monitoring compression H265 H.265 MJPEG Internal storage upto 8 SATA (Max 48 TB External storage 1 e-SATA Monitoring Web viewer and Mobile Viewer camera support ONVIF complete in all respects. as approved by the Engineer Incharge. | P/Job. | 2
LED MONITOR & LD TV & HARD DRIVE
52 | 8-8-01 (d) | Supply, installation, testing & commissioning of 55 " LED SMART TV Latest model suitable for operation on 220/230 v 50 hz Ac supply including usb /HDMI ports Video in audio in suitable to HDMI -1 To HDMI-11 via wire less remote flexible cord shoe WIFI blue tooth wall bracket wawal bolts etc complete with electric connections as approve dby the engineer in charge. | P/Job. | 12
POE SWITCHES
53 | 8-7-01(c) | providing fixing and installation poi giga bit switches 24-Port , including all components and accessories complete in all respect as approved by the Engineer in charge. | P/Job. | 4
B2. |  | GUARD ROOM ELECTRICAL WORKS
POINT WIRING IN RECESSED PVC CONDUIT
54 | 2-3-01 | Wiring for light or fan point with (3/.029") pvc insulated wire in 20 mm² (3/4") dia upvc conduit recessed in the wall , column , roof including 1 mm² single core pvc insulated wire as ECC as Required. | Point | 2
EXTENSION /ADDITIONAL POINT WIRING
55 | 2-7-03 | Extension /additional wiring for light fan call bell or light plug point controlled with same switch with (3/.029") pvc insulated wire in 20 mm (3/4") dia PVC conduit recessed in the wall , column or roof including 1mm² single core pvc insulated wire as ECC as required | P/Point | 3
2 WIRE WITH ECC WIRE IN EXISTING CONDUITS/CABLE DUCT
56 | 2-27-02 | Supply & drawing of 2 x2.5 mm² single core pvc insulated wire including 1 mm² pvc insulated wire single core wire as ECC in all kind of existing or given conduits /cable duct as required | Rft | 300
57 | 2-27-03 | Supply & drawing of 2 x4 mm² single core pvc insulated wire including 1.5 mm² pvc insulated wire single core wire as ECC in all kind of existing or given conduits /cable duct as required.(Db to first Socket , Socket to Socket) | Rft | 300
UPVC CONDUIT & DUCT
58 | 2-61-06 | Supply and fixing 20mm (3/4") dia Upvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 300
59 | 2-61-07 | Supply and fixing 25mm (1") dia pvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 500
SCHNEIDER /PHILIPS ACCESSORIES ON RESSED METAL BOARD
60 | 2-66-11 | Providing & fixing Polycarbonate flame retardant, 400 watts fan dimmer with plate fixed on die fabricated, powder coated, metal board recessed in the wall or column including connection as required. | Each | 1
ELECTRIC FANS
CEILING FAN
61 | 2-80-03 | Providing & installing 140 Cm (56") sweep ceiling fan with blades, canopy, standard length of down rod including connection with 14.0076" flexible wire complete as required. (without regulator) Millat / Pak / Asia / Younas / Climax / Royal. | Each | 1
WALL BRACKET FAN
62 | 2-81-01 | Providing & installing 35 Cm (14") wall bracket fan complete with blades, regulator & pulling cord switch, fitted on wall or column with GI clip including connection as required. Millat / Pak / Asia / Younas / Climax / Royal. | Each | 1
FAN CLAMPS
63 | 2-87-06 | Providing & fixing 3"x4"x5" size (14 SWG) thick recessed type fan clamp box with 1/2" dia MS bar fan clamp fixed in roof at casting time as required. | Each. | 1
DOUBLE ACTION PLASTIC BODY EXHAUST FANS
64 | 2-85-02 | Providing & installing 25 Cm (10") sweep Double action Plastic body exhaust fan complete with blades, motor & regulator & pulling cord switch etc. fixed in existing hole including connection with 14 /.0076" flexible wire complete as required. Millat / Pak / Asia / Younas / Climax / Royal. | Each | 1
(SUNLIGHT , PIERE LIGHT , FUTURE TECHNOLOGY)
65 | 2-78-01(a) | Supply installation testing & commissioning of recessed / surface mounted Ceiling light/down light including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (7-10) Watts | Each | 2
66 | 2-78-01(c) | Supply installation testing & commissioning of recessed / surface mounted Ceiling light/down light including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (18-20) Watts | Each | 2
B3. |  | OPERATOR ROOM ELECTRICAL WORKS
POINT WIRING IN RECESSED PVC CONDUIT
67 | 2-3-01 | Wiring for light or fan point with (3/.029") pvc insulated wire in 20 mm² (3/4") dia upvc conduit recessed in the wall , column , roof including 1 mm² single core pvc insulated wire as ECC as Required. | Point | 2
EXTENSION /ADDITIONAL POINT WIRING
68 | 2-7-03 | Extension /additional wiring for light fan call bell or light plug point controlled with same switch with (3/.029") pvc insulated wire in 20 mm (3/4") dia PVC conduit recessed in the wall , column or roof including 1mm² single core pvc insulated wire as ECC as required | P/Point | 3
2 WIRE WITH ECC WIRE IN EXISTING CONDUITS/CABLE DUCT
69 | 2-27-02 | Supply & drawing of 2 x2.5 mm² single core pvc insulated wire including 1 mm² pvc insulated wire single core wire as ECC in all kind of existing or given conduits /cable duct as required | Rft | 300
70 | 2-27-03 | Supply & drawing of 2 x4 mm² single core pvc insulated wire including 1.5 mm² pvc insulated wire single core wire as ECC in all kind of existing or given conduits /cable duct as required.(Db to first Socket , Socket to Socket) | Rft | 300
UPVC CONDUIT & DUCT
71 | 2-61-06 | Supply and fixing 20mm (3/4") dia Upvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 300
72 | 2-61-07 | Supply and fixing 25mm (1") dia pvc conduit with all especial such as bends, sockets, junction etc recessed in the wall or column as required | P/Rft | 500
(SUNLIGHT , PIERE LIGHT , FUTURE TECHNOLOGY)
73 | 2-78-01(a) | Supply installation testing & commissioning of recessed / surface mounted Ceiling light/down light including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (7-10) Watts | Each | 2
74 | 2-78-01(c) | Supply installation testing & commissioning of recessed / surface mounted Ceiling light/down light including driver having war/ neutral white / cool white colour 80-90 lm/ watt efficiency .9 or above power factor , 20000-25000 hours life cycle including connection complete in all respect as approved by the Engineer in charge. (18-20) Watts | Each | 2
COST OF SCHEDULED ITEM (Rs.) = | [5 empty] | 0
NON-SCHEDULED ITEMS
B4. |  | ELECTRICAL WORKS
Supply, installation, testing and commissioning of the following items of work (unless specifically stated otherwise) including all material, labour, tools, plant, accessories, related civil works, etc., required for proper completion of each item as per specifications (Section-8001 "General Specifications for Electrical Works" shall be applicable to all BOQ items).
MAIN SWITCHBOARDS /SUB MAIN DISTRIBUTION BOARDS
(Ref. Spec. 8001 , 8133)
Following Type tested(Form 4 B) L.T. Switchboard and Submain Distribution Boards, (as per single line diagram shown on the drawing), including all control wiring, foundation, related civil works and all accessories, complete in all respects. Make: Bilal Engineering, Ercon, Lineman , JEI)
54 | 1 | MDB | Job | 1
55 | 2 | EMDB | Job | 1
56 | 3 | ATS PANEL FOR 200 KVA GENSET | Job | 1
57 | 4 | DB-GF | Job | 1
58 | 5 | DB-FF | Job | 1
59 | 6 | ACDB-GF | Job | 1
60 | 7 | ACDB-FF | Job | 1
61 | 8 | DB-CL | Job | 1
62 | 9 | DB-TL | Job | 1
63 | 10 | DB-COM | Job | 1
64 | 11 | DB-TDL | Job | 1
65 | 12 | DB-TDL-II | Job | 1
66 | 13 | DB-FAL | Job | 1
LED LIGHT FIXTURE
(Ref. Spec. 8001, 8150)
Supply, installation, testing & commissioning of the following types of light fixtures including LED Light with driver, internal wiring complete with all mounting accessories as per architectural arrangements/ requirements, dust & moisture protected and corrosion proof and suitable for this area as acceptably supplied and installed and as approved by the Engineer.
67 | 14 | 12-15 Watt Wall Outdoor Decorative Light (IP-65) | Each | 45
68 | 15 | Supply and Installation of 6" dia PVC Class 'D' pipe | Rft | 600
69 | 16 | Supply and Installation of 3" dia PVC Class 'D' pipe | Rft | 180
70 | 17 | Supply and Installation of 4" dia PVC Class 'D' pipe | Rft | 150
WIRING ACCESSORIES
(Ref. Spec. Sec. 8001, 8220)
71 | 18 | 10 Amps, 250 Volts one way, ONE gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 30
72 | 19 | 10 Amps, 250 Volts one way, TWO gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 30
73 | 20 | 10 Amps, 250 Volts one way, THREE gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 10
74 | 21 | 10 Amps, 250 Volts one way, FOUR gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 6
75 | 22 | 10 Amps, 250 Volts one way, FIVE gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 12
76 | 23 | 10 Amps, 250 Volts one way, SIX gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 8
77 | 24 | Simplex Universal Switch outlet with switch 13 A, 230V. Mounting Height as per site including appropriate size powder coated metallic back box. | No. | 520
78 | 25 | 15 Amps, 250 Volts Universal switch socket unit including appropriate size powder coated metallic back box. | No. | 10
79 | 26 | 20 Amps, 250 Volts flex outlet with double pole switch & neon indication lamp including appropriate size steel back box & fuse protection | No. | 50
80 | 27 | 5 Pin 32 Amps, 400 Volts Industrial sockets along with size steel back box | No. | 30
Following sizes of Powder Coated perforated G.I. sheet cable trays with cover including joints, bend, mounting brackets hanger complete with all accessories.
81 | 28 | 12" x 3" | Rft. | 1000
82 | 29 | 6" x 2" | Rft. | 1000
EARTHING
(Ref. Spec. Sec. 8001, 8240)
83 | 30 | 305 mm long, 50 mm wide and 6mm thick copper busbar as ECP (Earth Connecting Point) complete with insulators, washers, nuts, bolts mounting installation and operational accessories as per site requirements. | Each | 10
84 | 31 | Test point for lightning system on down conductors, comprising 1/4" size copper terminals at 5'-0 above finished ground level protected with copper cover firmly fixed on column, complete in all respects. | No. | 10
STRUCTURED CABLING NETWORK(TELEPHONE & NETWORKING)
Ref.Spec. 8212,8230,8240,8290,8312
85 | 32 | Wiring of Telecommunication RJ45 outlet point from relevant Floor distributor Cabinet to RJ45 outlet point with CAT-6A, F/UTP 10G supported cable including appropriate size concealed or surface PVC conduit or PVC channel , all accessories with cutting/making holes in walls making surface good complete in all respect. | No. | 200
86 | 33 | (2 X 25) 50 pair Cat-5 UTP cable for voice back bone including Appropriate size trunking / conduit complete in all respect. | Rft. | 400
Following type CAT-6A, F/UTP Giga Speed patch cord with required connector at both ends:
87 | 34 | 1 metre (3 ft.) long | No. | 200
88 | 35 | 3 metre (10 ft.) long | No. | 200
89 | 36 | Simplex Face plate with RJ-45 I/0 CAT-6 F/UTP telecommunication outlet including sheet steel back box shall make of 16 SWG shall be finished in powder coated paint. including all mounting accessories. | No. | 160
90 | 37 | 24 port Cat-6A F/UTP 10G Supported modular (RJ45) jack (Loaded with (RJ45) jack) patch panels compatible 19" rack installed in floor/wall mounted cabinet including built-in rear cable management with all mounting accessories. | No. | 9
91 | 38 | 19" Rack mounted Front Cable Management. | No. | 9
92 | 39 | 1m long patch cord with RJ45 connector at one end and required IDC connector at another end. | No. | 40
93 | 40 | 1m long single pair patch cord with required connector at both ends. | No. | 40
Following type disconnection module with all mounting accessories.
94 | 41 | 50 pair | No. | 2
Following sizes Rack with Plexiglass door including Hoops, side management, cable trays, fan tray and required number of power sockets including all mounting accessories.
95 | 42 | 18 U | No. | 10
96 | 43 | Supply installation testing and commissioning of layer-2 network switch with 24 Giga Ethernet ports with 02 Nos of SFPS OM3 Up Link (Support 10.0 G ) Including Cost of 02 Nos 10G SFP OM3 up link (support 10.0 G) including cost of 02 Nos 10 G SFPS Modules Multi mode complete in all respect. | No | 9
97 | 44 | Supply, Installation, Testing & Commissioning of WIFI Access Points Ceiling Mounted Support 802.11 a/g/n, Software Ctrlr-based, Long Range, Complete in all respect, as per drawing and specifications. | No | 30
98 | 45 | 50 pair telephone junction box (TJB) for required number of incoming and outgoing cables, appropriate back box complete in all respect. | No. | 2
TELEPHONE EXCHANGE SYSTEM
Ref.Spec. 8212,8230,8240,8290,8312
99 | 46 | Supply, Installation, testing and commissioning of Hybrid IP-EPABX, for 16 Trunk with 200 extensions upgradable to 16, Proprietary Basic shelf with expansion shelf, IP Gateway, Call logging software with PC , OGM Card for auto call attendant, 60 Minutes Backup Power Supply for IP-EPABX Operator Console with accessories . Slave connection circuit , Digital Extension Card Caller ID Card Shelf Connection card for Basic shelf Back ground music on hold and Console with all required Power supply cards. EPABX Exchange shall include all standard Cards. | Job | 1
100 | 47 | Executive Telephone Sets with CLI | No | 20
IP BASED PUBLIC ADDRESS SYSTEM
(Ref. Spec. Sec. 8001, 8341)
101 | 48 | Supply, installation and commissioning of speakers wiring, to be wired with PVC insulated,PVC sheathed LSZH twin core 1.5 mm2 flexible shielded control wire in 3/4" dia PVC conduit with all necessary fitting accessories, pull boxes, steel pull wires, complete in all respects. | Rft | 5500
102 | 49 | Supply, installation and commissioning of Table Top Digital Microphone, Uni-directional, condensor microphone with PTT (Push to Talk) and Status LED complete in all respect as Approved by the Engineer Incharge. | No. | 12
103 | 50 | Supply, installation and commissioning of 30 Watt Column speaker & tapping, suitable for both speech and music, 90 Hz to 20 KHz, Flush Mount including all accessories complete in all respect as Approved by the Engineer Incharge. | No. | 28
104 | 51 | Supply, installation and commissioning of Ceiling speaker 6 Watt rated & tapping, suitable for both speech and music, 90 Hz to 20 KHz, Flush Mount including all accessories complete in all respect as Approved by the Engineer Incharge. | No. | 4
105 | 52 | Supply, installation and commissioning of Digital Mixer IP Based Amplifier built in 240W, 4 mic inputs, music input. 190-220V operating voltage as Approved by the Engineer Incharge. | No. | 11
106 | 53 | 6 U Rack with Plexiglass door including Hoops, side management, cable trays, fan tray and required number of power sockets including all mounting accessories. For Public Addres System | No. | 11
SOLAR SYSTEM (PHOTOVOLTAIC)
107 | 54 | Supply and Erection of hot dipped (80 microns Average) galvanized steel of minimum thickness of 14 SWG / Channel / Pipe or 8 SWG / 4.06 mm Angle , GRID TIE INVERTER (ON-Grid Inverter) , Stainless Steel Nuts and Bolts , (XPLE/XPLO insulated/PCV sheathed) flexible copper cables , conduits/Pvc Duct , wiring , power cables , MC4 Branch connector , MC4 connector (TUV Approved) , Earthing , lightning protection ,Lightning Arrestor 1" Copper rod 6ft long with 4'' Bowl five spikes complete in all respect (above top structure level) , powder coated perforated cable tray , civil Work complete in all respect as approved by the Engineer. | Watt | 300000
GREEN ENERGY METER & CONTROL EQUIPMENT
108 | 55 | Supply and Erection of Green Meter including Certification Regulations or Related NEPRA and PESCO Fee for installation and Activation of Green Energy Meter include Grid Flow Study from approved consultant of PESCO | Job | 2
109 | 56 | Providing Fixing and Configuration of Gen Set Controller with all Mounting and Control Accessories | Job | 1
110 | 57 | Providing Fixing of water Proof Type DC Distribution box MCB/FUSES for Each Strings (for each Inverter) including DC Breakers SPD with Terminals Complete in all respects | Job | 6
111 | 58 | Providing and Fixing of Weather station includes Wind Speed humidity,Ambbient temperature module Temperature control cable complete in all respect | Job | 1
112 | 59 | Providing and Fixing of Monitoring and Communication OEM Logger (4G Dongle) | Job | 2
MAIN SWITCHBOARDS /SUB MAIN DISTRIBUTION BOARDS
(Ref. Spec. 8001 , 8133)
Following Type tested (Form 4 B) L.T. Switchboard and Submain Distribution Boards, (as per single line diagram shown on the drawing), including all control wiring, foundation, related civil works and all accessories, complete in all respects. Make: Bilal Engineering, Ercon, Lineman , JEI)
113 | 60 | MDB-SOLAR PANEL-01 | Job | 1
114 | 61 | MDB-SOLAR PANEL-02 | Job | 1
CABLE PULLING PIT (4'X4'X4')
115 | 62 | Cable pulling pit (4' X 4' X 4') made of RCC(1:2:4) and RCC cover with MS angle frame for easy pulling of cables including all accessories located as per drawings. | No | 4
116 | 63 | Sealing of conduits after cable pulling with jute & Plaster of Paris as per Engineer's Instructions. | No. | 4
B5. |  | GUARD ROOM ELECTRICAL WORKS
WIRING ACCESSORIES
(Ref. Spec. Sec. 8001, 8220)
117 | 64 | 10 Amps, 250 Volts one way, FOUR gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 1
118 | 65 | Simplex Universal Switch outlet with switch 13 A, 230V. Mounting Height as per site including appropriate size powder coated metallic back box. | No. | 4
B6. |  | OPERATOR ROOM ELECTRICAL WORKS
WIRING ACCESSORIES
(Ref. Spec. Sec. 8001, 8220)
119 | 66 | 10 Amps, 250 Volts one way, FOUR gang light control switches including appropriate size powder coated metallic concealed back box. | No. | 1
COST OF NON-SCHEDULED ITEM (Rs.) = | [5 empty] | 0
TOTAL COST OF SCHEDULED & NON-SCHEDULED ITEM (Rs.) = | [5 empty] | 0
RECOMMENDATION
6 No 50 kw on Grid Inverter
545 W Each Solar Panels
300 KW Systems

## 3. Plumbing
UNHCR PAKISTAN
CONSTRUCTION OF VOCATIONAL TRAINING INSTITUTE FOR WOMEN BUFFER ZONE, KARACHI
ENGINEER'S ESTIMATE
PLUMBING WORKS
ITEM No. | PAK PWD SCHEDULE 2022 REF No./NS | DESCRIPTION | UNIT | QTY. | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) |  | (b) | (c) | (d) | (e) | (f)
GENERAL NOTE
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per drawings, specifications and as approved by the Engineer.
C1. |  | BUILDING PLUMBING WORKS
SCHEDULED ITEMS
SANITARY FIXTURES AND FITTINGS
1 | 301-5 | Providing and fixing Pakistani best quality European style white glazed earthenware W.C pan complete with and including the cost of plastic seat with buffers, best quality low level plastic flushing cistern of standard size with internal fittings complete, P.V.C flushing pipe with fittings and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | Each | 7
2 | 301-28 | Providing and fixing best quality squatting type earthenware W.C pan (Porta or equivalent) complete with and including the cost of 13.6 liter best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe suitable for squatting type with extra bends and length with fittings, PVC trap 4 inches (100mm) dia and making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | Each | 7
3 | 301-17 | Providing 1/2 inch (15 mm) dia plastic connection complete with a 1/2 inch (15 mm) dia brass stop cock two brass nuts and lining jointed to plastic pipe. | Each | 42
4 | 301-25 + (4205) | Providing and fixing approved quality earthen ware glazed vanity basin standard size (White/light colour) and including the cost of Chromium plated mixer tap 1/2 inch dia, 1-1/4” dia brass waste 1-1/4” rubber plug and chrome plated brass chain PVC waste pipe 1-1/4” dia of approved pattern etc. complete. | Each | 14
5 | 301-21 | Providing and fixing approved quality stainless steel sink 60” x 20” Pak made (Atlas) or equivalent complete with brass oxidized bolt kit/angle iron brackets built into walls ½” dia CP sink mixer 1-1/4” rubber plug and CP brass chain 1-1/4” CP brass waste 1-1/4” dia malleable iron or CP brass bottle trap with malleable iron or brass unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4 | Each | 4
6 | 302-2 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | Each | 5
7 | 302-3 | Providing and fixing approved quality C.P. brass toilet paper holder. | Each | 7
8 | 302-13 | Providing and fixing chromium plated Muslim bib-cock with muslim shower of approved quality. | Each | 14
9 | 307-2 | Providing and fixing 1/2 inches dia. (15 mm) CP Bib cocks. | Each. | 1
10 | 309-30 | Providing and fixing water tank made of food grade polyethylene material 1000 gallon (Super tuff) i/c cost of specials and cartage upto site as per direction of Engineer incharge. | Each. | 2
WATER SUPPLY PIPES AND FITTINGS
11 |  | Providing G.I. pipes, specials and clamps etc., including fixing, cutting and fitting, complete with and including the cost of breaking through walls and roof, making good etc., painting 2 coats after cleaning the pipe etc. with white zinc paint with pigment to match the colour of the building and testing with water to a pressure head of 200 feet (61 m) and cartages within 10 miles. (16.09km). (ILLM). of following pipe sizes:
| 305-2 | 3/4 inch (20mm) dia pipe | Rft | 20
| 305-3 | 1 inch (25mm) dia pipe | Rft | 110
| 305-4 | 1-1/4 inch (32mm) dia pipe | Rft | 60
| 305-5 | 1-1/2 inch (40mm) dia pipe | Rft | 200
| 305-6 | 2 inch (50mm) dia pipe | Rft | 10
12 |  | Providing and fixing PPRC pipe PN-20 with specials and clamps etc, including cutting and fitting complete with and including the cost of breaking through walls and roof and making good etc: after cleaning the pipe and cartage within 10 miles.
| 306-30 | 25mm dia | Rft | 80
| 306-31 | 32mm dia | Rft | 320
| 306-32 | 40mm dia | Rft | 150
| 306-33 | 50mm dia | Rft | 50
| 306-34 | 63mm dia | Rft | 20
13 |  | Providing and fixing full way gun metal valves with wheels threaded or flanged ends with rubber washers, (standard pattern) of following diameters:
| 307-8 | 3/4 inch (20mm) dia | Each | 16
| 307-9 | 1 inch (25mm) dia | Each | 17
| 307-10 | 1-1/4 inch (32mm) dia | Each | 1
| 307-11 | 1-1/2 inch (40mm) dia | Each | 3
| 307-12 | 2 inch (50mm) dia | Each | 1
14 |  | Providing and fixing gun-metal non-return valves with male and female ends as required of following diameters: (For Electric water Heaters)
| 307-29 | 3/4 inch (20mm) dia | Each | 9
SOIL, WASTE AND VENT PIPES & FITTINGS
15 | 301-30 | Providing and fixing uPVC Multi floor trap of sizes with gratings including cutting and making requisite number of holes in walls, plinth and floors and making good in 1:2:4 C.C. | Each | 11
16 | 314-3 | Providing and fixing 6" x 6" (150 mm x 150 mm) with 4 inches (100 mm) outlet cement concrete C.I. gully trap wt: 42 Ibs. (19 kg.) complete with 4 inches thick (100 mm) 1:2:4 cement concrete for bed and kerb, 1/2 inch (13 mm) thick cement plaster (1:3) to the kerb, CI grating 6 inches x 6 inches (150mm x 150mm) and CI cover and frame 12" x 12" (305mm x 305mm) (inside) etc., complete... | Each | 6
C2. |  | EXTERNAL PLUMBING WORKS
EARTH WORK & PIPE TRENCHES
17 | 103-1 | Excavation for foundation trenches and drains in all kinds of soil (except gravelly and murum soil, wet silt, clay or mud conglomeration of gravel and boulders, soft, sandy or disintegrated sandy and hard rock) and back filling the excavated material in foundation, plinth or under floor including breaking clods, watering, consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction, dressing and disposal of surplus excavated stuff as directed, lead upto one chain (30.5 R.m) and lift upto 5 feet (1.52 m). | 100 Cft | 18000
18 | 104-9 | Supplying stacking and filling sand of approved quality from outside sources in foundation, trenches, plinth or under floor, etc. including dressing, watering and consolidation by ramming in layers not exceeding 9 inches (229 mm) in depth to full compaction and lift upto 5 feet (1 .52 m). | 100 Cft | 7700
19 | 106-5 + 106-32 + 106-52 | Providing and laying in situ 1:2:4 (1 cement 2 sand and 4 coarse aggregates) cement concrete using 50% crushed graded bolders 3/4" (19mm) and down gauge and 50% graded screened bajri 3/4" (19mm) and down gauge with lawancepur sand in foundation, basement and plinth including formwork, compacting, curing and removal of formwork etc. complete foundation and basements upto 5 feet depth (1.52m) and plinth upto 4 feet(1.2m) height from ground level. (For concrete encasement and thrust blocks) | 100Cft | 400
WATER SUPPLY PIPES AND FITTINGS
20 |  | Providing G.I. pipes and specials, etc.; including fixing, cutting and fitting, complete with and including the cost of cutting trench upto 2-1/2 feet (762 mm) deep, refilling, watering, ramming and disposal of surplus earth within one chain and painting 2 coats of bitumen paint to pipes and specials after cleaning and hessian cloth soaked in maxphalt composition wrapped tightly round the pipes and testing to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM).
| 306-5 | 1-1/2 inches (40 mm) dia pipe (ILLM). | Rft | 40
| 306-6 | 2 inches (50 mm) dia pipe (ILLM). | Rft | 10
21 |  | Providing and fixing PPRC pipe PN-20 with specials and clamps etc, including cutting and fitting complete with and including the cost of breaking through walls and roof and making good etc: after cleaning the pipe and cartage within 10miles.
| 306-32 | 40mm dia | Rft | 100
22 |  | Providing and fixing full way gun metal valves with wheels threaded or flanged ends with rubber washers, (standard pattern) of following diameters:
| 307-11 | 1-1/2 inch (40mm) dia | Each | 1
| 307-12 | 2 inch (50mm) dia | Each | 1
23 | 307-21 | Providing and fixing 1-1/2 inches (40mm) dia ball valve (with PVC Ball) made to B.S.S. 1212 | Each | 1
CI MANHOLE COVERS
24 | 315-27 | Providing and & fixing C.I Cover & Frame 24'' dia (610mm) weight 2 cwt 2Qtr (127.00kg.) | Each | 17
C3. |  | UNDERGROUND WATER TANK
WATER SUPPLY PIPES AND FITTINGS
25 |  | Providing G.I. pipes, specials and clamps etc., including fixing, cutting and fitting, complete with and including the cost of breaking through walls and roof, making good etc., painting 2 coats after cleaning the pipe etc. with white zinc paint with pigment to match the colour of the building and testing with water to a pressure head of 200 feet (61 m) and cartage within 10 miles. (16.09km). (ILLM). of following pipe sizes: (For Drainage pipe and Drainage pump)
| 305-6 | 2 inch (50mm) dia pipe | Rft | 50
26 |  | Providing and fixing full way gun metal valves with wheels threaded or flanged ends with rubber washers, (standard pattern) of following diameters:
| 307-12 | 2 inch (50mm) dia | Each | 1
27 |  | Providing and fixing gun-metal non-return valves with male and female ends as required of following diameters:
| 307-33 | 2 inch (50mm) dia | Each | 1
28 | 315-28 | Providing & fixing C.I Cover & Frame 30" dia (765 mm) weight 3 cwt (152.41 Kg.) | Each | 2
C4. |  | GUARD ROOM PLUMBING WORKS
SANITARY FIXTURES AND FITTINGS
29 | 301-28 | Providing and fixing best quality squatting type earthenware W.C pan (Porta or equivalent) complete with and including the cost of 13.6 liter best quality low level plastic flushing cistern with internal fittings complete, P.V.C flushing pipe suitable for squatting type with extra bends and length with fittings, PVC trap 4 inches (100mm) dia and making requisite number of holes in walls, plinth and floor for pipe connection and making good in cement concrete 1:2:4. | Each | 1
30 | 301-9 | Providing and fixing 22inches x 16inches (560mm x406mm) lavatory basin in white glazed earthenware (Pakistani) complete with and including the cost of Brass oxidized bolts kit built into wall 1/2 inch (15mm) dia. Chrome plated mixer 1-1/4 inches(32 mm) rubber plug and chrome plated brass chain,1-1/4 inches(32mm) dia. brass waste of approved pattern, 1-1/4 inches (32mm) dia chromium plated bottle trap with unions and making requisite number of holes in walls, plinth and floor for pipe connections and making good in cement concrete 1:2:4. | Each | 1
31 | 301-17 | Providing 1/2 inch (15 mm) dia plastic connection complete with a 1/2 inch (15 mm) dia brass stop cock two brass nuts and lining jointed to plastic pipe. | Each | 3
32 | 302-2 | Providing and fixing 24"x3/4"(610 mm x 20 mm) dia approved quality of chrome plated brass towel rail complete with brackets fixed with 1"(25 mm) long C.P brass screws and rawal plug. | Each | 1
33 | 302-5 | Providing and fixing 24inches x 18 inches (610mm x457mm) looking mirror of imported glass 5mm thick fixing with CP clamps and screws. | Each | 1
34 | 302-7 | Providing and fixing glass shelf 25 inches x 5 inches (610mm x 127mm) brackets and guard rail complete. | Each | 1
35 | 302-13 | Providing and fixing chromium plated Muslim bib-cock with muslim shower of approved quality. | Each | 1
36 | 307-2 | Providing and fixing 1/2 inches dia. (15 mm) brass bib cocks. | Each. | 1
WATER SUPPLY PIPES AND FITTINGS
37 |  | Providing and fixing PPRC pipe PN-20 with specials and clamps etc, including cutting and fitting complete with and including the cost of breaking through walls and roof and making good etc: after cleaning the pipe and cartage within 10miles.
| 306-30 | 25mm dia | Rft | 10
38 |  | Providing and fixing full way gun metal valves with wheels threaded or flanged ends with rubber washers, (standard pattern) of following diameters:
| 307-8 | 3/4 inch (20mm) dia | Each | 1
SOIL, WASTE AND VENT PIPES & FITTINGS
39 | 301-30 | Providing and fixing uPVC Multi floor trap of sizes with gratings including cutting and making requisite number of holes in walls, plinth and floors and making good in 1:2:4 C.C. | Each | 1
40 | 314-3 | Providing and fixing 6" x 6" (150 mm x 150 mm) with 4 inches (100 mm) outlet cement concrete C.I. gully trap wt: 42 Ibs. (19 kg.) complete with 4 inches thick (100 mm) 1:2:4 cement concrete for bed and kerb, 1/2 inch (13 mm) thick cement plaster (1:3) to the kerb, CI grating 6 inches x 6 inches (150mm x 150mm) and CI cover and frame 12" x 12" (305mm x 305mm) (inside) etc., complete. | Each | 1
COST OF SCHEDULED ITEM (Rs.) = | [5 empty] | 0
NON-SCHEDULED ITEMS
C5. |  | BUILDING PLUMBING WORKS
SANITARY FIXTURES AND FITTINGS
(Ref. Specs 5100)
41 | 1 | 05mm thick Glass mirror Belgium make or approved equivalent including hard board behind it, approved beeding around it and all other fittings for complete installation | Sft | 160
42 | 2 | CP Soap Dish of any shape, pattern and size, of approved make, complete with plugs, screws etc., fixed to concrete, brick, stone or wood work, complete in all respects . | Each | 7
43 | 3 | CP Soap Dispenser of any shape, pattern and size, of approved make, complete with plugs, screws etc., fixed to concrete, brick, stone or wood work, complete in all respects . | Each | 3
44 | 4 | Grab bar/Hand rail set (02 pc's) for handicap toilet commode with fixing plugs and screws etc. fixed to concrete, brick, stone or wood work, complete in all respects. | Each | 2
45 | 5 | Small hook of any size and shape, of approved make, with plugs and screws, fixed to concrete, brick stone or wood work, complete in all respects. | Each | 14
46 | 6 | Electric water heater of 8 gallons (30-40 Liters) capacity, including 02 Nos. Tee Stop cock, automatic temperature/pressure relief valve on outlet and all other accessories for complete installation. | Each. | 9
47 | 7 | Electric Hand Drier (automatic) of approved make & model and all required accessories complete. | Each. | 3
48 | 8 | Electric water cooler of 35 gallons capacity, including all accessories for complete installation. | Each | 2
49 | 9 | Water filter of following type, including all accessories for complete installation.
| (a) | Triple type filter | Each | 2
WATER SUPPLY PIPES AND FITTINGS
(Ref. Specs 5100, 5216, 5220)
50 | 10 | G.I pipes conforming to ASTM A-53 Sch. 40, including all fittings, cutting, welding & flange provisions, fixing, supports & hangers system as per requirement; cost of breaking and making holes through walls and slabs, making walls & slabs good thereafter, painting with two coats of enamel paint after cleaning the pipe, etc of approved make, complete in all respect. (Filling pipe)
| (a) | Dia 2.5 inch | Rft | 30
| (b) | Dia 2 inch | Rft | 100
51 | 11 | 01" thick Glass wool thermal insulation for cold and hot water GI pipes (in exposed conditions) including aluminium vapour barrier and GI (28swg) cladding and all other required accessories complete for following pipe diameters
| (a) | 3/4 inch (20mm) dia pipe | Rft | 10
| (b) | 1 inch (25mm) dia pipe | Rft | 50
| (c) | 1-1/4 inch (32mm) dia pipe | Rft | 60
| (d) | 1-1/2 inch (40mm) dia pipe | Rft | 200
| (e) | 2 inch (50mm) dia pipe | Rft | 10
52 | 12 | Air relief valves, of approved manufacturers, including jointing arrangement of valves; nuts, bolts etc. complete in all respects.
| (a) | 3/4 inches | Each | 6
SOIL, WASTE AND VENT PIPES & FITTINGS
(Ref. Specs 5100)
53 | 13 | uPVC Soil, Waste and vent pipes conforming to ISO:3633 type "B" or BS-4514/5255 class "A" of the following diameters, including imported rubber ring/solvent cement fittings, hangers & supports, jointing, cutting, breaking concrete/masonry and then making it good, core cutting & filling with non shrink grout of approved manufacturer wherever required and applying painting, cleaning and testing etc. complete in all respects.
| (a) | 1-1/2 inches | Rft | 130
| (b) | 2 inches | Rft | 210
| (c) | 3 inches | Rft | 230
| (d) | 4 inches | Rft | 500
| (e) | 6 inches | Rft | 30
54 | 14 | 3"dia uPVC Floor Trap with Stainless Steel-304 Top Tile strainer; supports; making required number of connections; breaking concrete or masonry work & then making it good; etc. | Each | 14
55 | 15 | uPVC Floor Cleanout of the following diameter, including Stainless Steel-304 top tile access plug, transition pipe, breaking concrete or masonry work & then making it good, etc. complete in all respects.
| (a) | 3 inches | Each | 1
| (b) | 4 inches | Each | 6
56 | 16 | uPVC Cowl on vent pipes of the following diameter.
| (a) | 3 inches | Each | 5
| (b) | 4 inches | Each | 4
STORM DRAINAGE PIPES & FITTINGS
(Ref. Specs 5100)
57 | 17 | uPVC Rain water pipes conforming to ISO:3633 type "B" or BS-4514/5255 class "A" of the following diameters, including imported rubber ring/solvent cement fittings, jointing, cutting, and breaking concrete/masonry and then making it good, applying painting, cleaning and testing etc. complete in all respects.
| (a) | 3 inches | Rft | 10
| (b) | 4 inches | Rft | 150
| (c) | 6 inches | Rft | 200
58 | 18 | CI roof drain of approved make of following diameters, including strainer, flushing material, and all accessories for complete installation, as per specifications.
| (a) | 3 inches | Each | 1
| (b) | 4 inches | Each | 2
| (c) | 6 inches | Each | 4
C6. |  | BUILDING FIRE FIGHTING WORKS
(Ref. Specs 5150, 5216)
59 | 19 | MS pipes conforming to ASTM A-53 Sch. 40, including all fittings, cutting, welding & flange provisions, fixing, supports & hangers system as per requirement; cost of breaking and making holes through walls and slabs, making walls & slabs good thereafter, painting with two coats of enamel paint after cleaning the pipe, etc of approved make, complete in all respect.
| (a) | Dia 1 inch (25 mm) | Rft | 10
| (b) | Dia 1-1/2 inch (40 mm) | Rft | 20
| (c) | Dia 2 inch (50 mm) | Rft | 10
| (d) | Dia 4 inch (100 mm) | Rft | 50
60 | 20 | Fire Hose Cabinet containing 1" dia and 100 ft long swing type fire hose reel with pressure reducing valve, gate valve and pressure gauge complete in all respect. | Each | 4
61 | 21 | Fire Extinguisher of following types.
| (a) | Dry Chemical Powder Fire Extinguisher 6Kg Capacity. | Each | 4
| (b) | Foam Type fire extinguisher capacity 9 litres. | Each | 4
| (c) | Wet Chemical fire extinguisher capacity 6 litres. | Each | 1
C7. |  | EXTERNAL PLUMBING WORKS
WATER SUPPLY PIPES AND FITTINGS
(Ref. Specs: 5216)
62 | 22 | Providing and laying HDPE Pipe (PN-12.5 & PE-100) conforming to ISO 4427:1996, DIN 8074/8075 with Compression / Butt fusion fittings and specials (as required) in pipe trenches, including flanges (BS-4504; PN-16 where required) and flushing, cleaning and disinfecting as per specifications and as directed by the Engineer of following diameters.
| (a) | 63mm | Rft | 350
63 | 23 | G.I pipes conforming to ASTM A-53 Sch. 40, including all fittings, cutting, welding & flange provisions, fixing, supports & hangers system as per requirement; cost of breaking and making holes through walls and slabs, making walls & slabs good thereafter, giving anti-corrosive treatment to pipe as per specifications etc., of approved make, complete in all respect. (Filling pipe)
| (a) | 2.5 inches | Rft | 100
SEWAGE PIPES
(Ref. Specs: 5100)
64 | 24 | uPVC non-pressure pipes for sanitary drainage conforming to BS-5481/BS-4660/EN-1401 (SN8) with rubber ring fittings and specials compatible with pipe material as per manufacturer's recommendations, complete in all respects, flushing cleaning and disinfecting as per specifications and as directed by the Engineer of following diameters.
| (a) | 160mm | Rft | 10
| (b) | 250mm | Rft | 400
C8. |  | EXTERNAL FIRE FIGHTING WORKS
(Ref. Specs: 5216, 5150, 5220, 5230)
65 | 25 | Providing and laying HDPE Pipe (PN-16 & PE-100) conforming to ISO 4427:1996, DIN 8074/8075 with Compression / Butt fusion fittings and specials (as required) in pipe trenches, including flanges (BS-4504; PN-16 where required) and flushing, cleaning and disinfecting as per specifications and as directed by the Engineer of following diameters.
| (a) | 125mm | Rft | 450
66 | 26 | C.I. gate valves conforming to BS-5163 (PN-16) including Adapters, flanges, nuts & bolts, transition pipe pieces with flanges, rubber seal, making required type of joints on both ends complete in all respect as shown on drawings or as directed by the Engineer of following diameters.
| a) | 4" dia | Each | 2
67 | 27 | Two way Breeching Inlet of PN-16 rating with integral check valve and drain valve; including cabinet, jointing and sealing arrangements and all other accessories complete in all respects. (NFPA Compliance) | Each | 1
68 | 28 | Bitumen coated cast Iron cover with frame conforming to BS-497, on valve chamber, including all fittings for complete installation.
| (a) | 36"x 36"(150kg) | Each | 2
C9. |  | UNDERGROUND WATER TANK
PUMPING MACHINERY
(Ref. Specs: 5240)
69 | 29 | Automatically operated pump set for lifting water from Underground water tank to Overhead water tank, consisting of 02 Nos. Potable Water Horizontal end suction Centrifugal pumps (one working, one standby) with electric motors and level switches to be installed in over head & underground water tank for automatic operation of pumps at set levels, automatic duty cycle relay, motor control unit, dry running protection, pressure gauges, manual, tools, spare parts and all other accessories complete in all respects; each of following Capacity and Pumping head.
|  | Capacity = 50 Igpm | Job | 1
Head = 100 feet
70 | 30 | Fire-fighting pumping unit (NFPA compliance) consisting of 02 Nos. Horizontal centrifugal Main Pumps (both Electric) each of Q=100USgpm & H=06Bars and 01 No. vertical centrifugal Jockey pump of Q=15USgpm & H=07 Bars with electric motor, including motor control units, 100 Liters Pressure Tank and all other accessories, automatic recirculation/pressure relief valve, gate valves, check valves, air release valve, pressure switches, pressure gauges, strainers, manual, tools, spare parts etc., complete in all respects. | Job | 1
71 | 31 | Automatically operated submersible drainage pump (01 No.) with electric motor (minimum particle passage : 25mm) including all accessories, control panel, level switches, manual, tools, spare parts etc, complete in all respect; of the following Capacity and Pumping head.
|  | Capacity = 30 Igpm | Job | 1
Head = 40 feet
GI WATER SUPPLY PIPES AND FITTINGS
(Ref. Specs: 5216)
72 | 32 | G.I pipes conforming to ASTM A-53 Sch. 40, including all fittings, cutting, welding & flange provisions, fixing, supports & hangers system as per requirement; cost of breaking and making holes through walls and slabs, making walls & slabs good thereafter, painting with two coats of enamel paint after cleaning the pipe, etc of approved make, complete in all respect. (with Potable water pumps)
| (a) | 2 inches | Rft | 40
| (b) | 2.5 inches | Rft | 20
MS FIRE FIGHTING WATER PIPES AND FITTINGS
(Ref. Specs: 5150, 5216)
73 | 33 | MS pipes conforming to ASTM A-53 Sch. 40, including all fittings, cutting, welding & flange provisions, fixing, supports & hangers system as per requirement; cost of breaking and making holes through walls and slabs, making walls & slabs good thereafter, painting with two coats of enamel paint after cleaning the pipe, etc of approved make, complete in all respect. (With Fire Fighting Pumps)
| (a) | 2 inches | Rft | 20
| (b) | 4 inches | Rft | 70
VALVES
(Ref. Specs: 5220)
74 | 34 | C.I. gate valves conforming to BS-5163 (PN-16) including Adapters, flanges, nuts & bolts, transition pipe pieces with flanges, rubber seal, making required type of joints on both ends complete in all respect as shown on drawings or as directed by the Engineer of following diameters.
| (a) | 4" dia | Each | 2
| (b) | 2.5" dia | Each | 1
| (c) | 2" dia | Each | 7
75 | 35 | C.I. check valves conforming to BS-5153 (PN-16) including Adapters, flanges, nuts & bolts, transition pipe pieces with flanges, rubber seal, making required type of joints on both ends complete in all respect as shown on drawings or as directed by the Engineer of following diameters.
| a) | 2" dia | Each | 2
76 | 36 | Flanged Expansion/Flexible Rubber joints (PN-16) including Adapters, flanges, nuts & bolts, transition pipe pieces with flanges, rubber seal, making required type of joints on both ends complete in all respect as shown on drawings or as directed by the Engineer of following diameters.
| (a) | 2" dia | Each | 1
| (b) | 4" dia | Each | 1
77 | 37 | Cast Iron Y-strainer BS standard (PN-16) of following nominal sizes including jointing arrangement etc. complete in all respects as per standards, manufacturer's recommendations, and as directed by the Engineer.
| (a) | 2" dia | Each | 1
MISCELLANEOUS
(Ref. Specs: 5100, 5230, 5150)
78 | 38 | 3/4inch diameter Galvanised MS ladder rungs for water tanks; each rung of 18inch width, 6inch projected outside the wall and 6inch embeded in RCC on both ends; including all necessary works for complete installation. | Each | 16
79 | 39 | Dia 4-inch u-turned G.I. vent pipes, puddle plate, with insect proof mesh at open end etc., complete in all respects. | Job | 2
80 | 40 | Bitumen coated cast Iron cover with frame conforming to BS-497, including all fittings for complete installation.
| (a) | 36"x 36"(150kg) | Each | 1
81 | 41 | Bitumen coated cast Iron Grating cover with frame conforming to BS-497, on sump pit in pump room, including all fittings for complete installation.
| (a) | 24" x 24"(60kg) | Each | 1
82 | 42 | Dry Chemical Powder Fire Extinguisher 6Kg Capacity. | Each | 2
RAIN WATER PIPES AND FITTINGS
(Ref. Specs: 5100)
83 | 43 | uPVC Rain water pipes conforming to ISO:3633 type "B" or BS-4514/5255 class "A" of the following diameters, including imported rubber ring/solvent cement fittings, jointing, cutting, and breaking concrete/masonry and then making it good, applying painting, cleaning and testing etc. complete in all respects.
| (a) | 04 inches | Rft | 10
84 | 44 | CI roof drain of approved make of following diameters, including strainer, flushing material, and all accessories for complete installation, as per specifications.
| (a) | 4 inches | Each | 1
C10. |  | GUARD ROOM PLUMBING WORKS
SANITARY FIXTURES AND FITTINGS
(Ref. Specs 5100)
85 | 45 | CP Soap Dish of any shape, pattern and size, of approved make, complete with plugs, screws etc., fixed to concrete, brick, stone or wood work, complete in all respects . | Each | 1
86 | 46 | Small hook of any size and shape, of approved make, with plugs and screws, fixed to concrete, brick stone or wood work, complete in all respects. | Each | 1
87 | 47 | Electric water heater of 8 gallons (30-40 Liters) capacity, including 02 Nos. Tee Stop cock, automatic temperature/pressure relief valve on outlet and all other accessories for complete installation. | Each. | 1
SOIL, WASTE AND VENT PIPES & FITTINGS
(Ref. Specs 5100)
88 | 48 | uPVC Soil, Waste and vent pipes conforming to ISO:3633 type "B" or BS-4514/5255 class "A" of the following diameters, including imported rubber ring/solvent cement fittings, hangers & supports, jointing, cutting, breaking concrete/masonry and then making it good, core cutting & filling with non shrink grout of approved manufacturer wherever required and applying painting, cleaning and testing etc. complete in all respects.
| (a) | 2 inches | Rft | 10
| (b) | 3 inches | Rft | 10
| (c) | 4 inches | Rft | 20
89 | 49 | Cawal on vent pipes of the following diameter.
| (a) | 2 inches | Each | 1
STORM DRAINAGE PIPES & FITTINGS
(Ref. Specs 5100)
90 | 50 | uPVC Rain water pipes conforming to ISO:3633 type "B" or BS-4514/5255 class "A" of the following diameters, including imported rubber ring/solvent cement fittings, jointing, cutting, and breaking concrete/masonry and then making it good, applying painting, cleaning and testing etc. complete in all respects.
| (a) | 04 inches | Rft | 10
91 | 51 | CI roof drain of approved make of following diameters, including strainer, flushing material, and all accessories for complete installation, as per specifications.
| (a) | 4 inches | Each | 1
FIRE EXTINGUISHER
92 | 52 | Dry Chemical Powder Fire Extinguisher 6Kg Capacity. | Each | 1
COST OF NON-SCHEDULED ITEM (Rs.) = | [5 empty] | 0
TOTAL COST OF SCHEDULED & NON-SCHEDULED ITEM (Rs.) = | [5 empty] | 0

## 4. Natural Gas
UNHCR PAKISTAN
CONSTRUCTION OF VOCATIONAL TRAINING INSTITUTE FOR WOMEN BUFFER ZONE, KARACHI
ENGINEER'S ESTIMATE
NATURAL GAS SUPPLY WORKS
ITEM No. | PAK PWD SCHEDULE 2022 REF No./NS | DESCRIPTION | UNIT | QTY. | UNIT RATE (Rs.) | TOTAL AMOUNT (Rs.)
(a) |  | (b) | (c) | (d) | (e) | (f)
GENERAL NOTE
Entire work will be executed by SSGC or their approved Contractors.
Supply, installation, testing and commissioning of the following items of work, including all labour, tools, plant, accessories, etc. required for completion of each item as per drawings, specifications and as approved by the Engineer.
D1. |  | SCHEDULED ITEMS
1 | 4-1-01 | Providing and fixing low pressure gas G.I. pipe (medium) with special such as bend, Tee, union and socket etc as required.
|  | 13mm (1/2") dia | Rft | 40
|  | 20mm (3/4") dia | Rft | 150
|  | 25mm (1") dia | Rft | 150
|  | 30mm (1-1/4") dia | Rft | 10
2 | 4-1-02 | Providing and fixing brass gas cock as required
| b | 15mm (1/2") dia | Each | 4
3 | 4-1-04 | 1st coat of painting on new or old work such as pipes and similar works not exceeding 150mm internal dia with aluminium paint/pigment to match the colour of other components as required. | Rft | 50
4 | 4-1-05 | 2nd subsequent coat of painting on new or old work such as pipes and similar works not exceeding 150mm internal dia with aluminium paint/pigment to match the colour of other components as required. | Rft | 50
5 | 4-2-07 | Providing and fixing Audco valve as required.
| b | 25mm (1") dia | Each | 1
6 | 4-2-10 | Providing and fixing Gas regulator as required.
| b | (043) Type | Each | 1
7 | 316-5 | Applying two coats of anticorrosive bitumen paint of approved quality on iron work pipe etc. | Sft | 100
8 | 316-6 | Providing and wrapping tightly round pipes upto 6 inches (150mm) dia Hessian soaked in bitumen paint of approved quality. | Rft | 300
9 | 4-3-19 | Providing, fixing, testing and commissioning of Gas detector with allied components, complete in all respect as approved by the Engineer Incharge. | Each | 2
TOTAL COST OF SCHEDULED ITEM (Rs.) = | [5 empty] | 0

## All Block (hidden)
D H Q HOSPITAL BANNU OPD / ADMIN BLOCK
MEASUREMENT SHEET
S.NO | Description | NO | L | B | H | QTY | UNIT
GROUND FLOOR
Earth work
C-01 | Earth fill in lawns | 1 | 100 |  |  | 100 | Cft
C-02 | Earth Under Floor | 1 | 12323 | 0.5 | 0.25 | 1540.375 | Cft
C-03 | Extra lead 15 m | 1 | 15546 |  |  | 15546 | Cft
C-04 | Transportation 250 to 500m. | 1 | 15546 |  |  | 15548 | Cft
C-05 | Transportation 500m to 1.5 km | 1 | 15546 |  |  | 15546 | Cft
C-06 | Transportation 1.5 km to 8.0 km. | 1 | 15546 |  |  | 15546 | Cft
C-07 | Transportation beyond of 8.0 km. | 1 | 15546 |  |  | 15546 | Cft
| Excavation in Foundation Ordinary Soil |  | 12323 |  |  | 12323
| Excavation in Comon Material |  | 12323 |  |  | 12323
| Backfill using granular material |  | 100 |  |  | 100
| Dismantling brick work in lime or cement mortar |  | 100 |  |  | 100
| Dismantling cement block masonry |  | 100 |  |  | 100
| Dismantling : Plain Cement Concrete 1:4:8 |  | 100 |  |  | 100
| Dismantling : Plain Cement Concrete 1:3:6 |  | 10831 |  |  | 10831
| Dismantling : Plain Cement Concrete 1:2:4 |  | 100 |  |  | 100
| Dismantling RCC, separating reinforcement, cleaning & straightening the same |  |  |  |  | 100
| Scraping : Ordinary distemper, oil bound distemper or paint off wall (also on roof) |  |  |  |  | 41653
| Total Transportation |  |  |  |  | 77730 | Cft
| Transportation in five component |  |  |  |  | 15546 | Cft
C-08 | Excavation in Foundation Ordinary Soil | 1 | 12323 |  |  | 12323 | Cft
C-09 | Excavation in Comon Material | 1 | 12323 |  |  | 12323 | Cft
C-10 | Backfill using granular material | 1 | 100 |  |  | 100 | Cft
Dismantling ( Demolishing)
C-11 | Brick Work | 1 | 100 |  |  | 100 | Cft
C-12 | Block Masonary | 1 | 100 |  |  | 100 | Cft
C-13 | PCC 1:4:8 | 1 | 100 |  |  | 100 | Cft
C-14 | PCC 1:3:6 | 1 | 10831 |  |  | 10831 | Cft
C-15 | PCC 1:2:4 | 1 | 100 |  |  | 100 | Cft
C-16 | RCC Seprating Reinfocement Cleaning & Straightening | 1 | 100 |  |  | 100 | Cft
C-17 | Scraping Ordinary distemper, Oil Bound distemper | 1 | 41653 |  |  | 41653 | Sft
C-18 | Stone Ballast
| Stone Ballast undr pcc | 1 | 10831 |  |  | 10831
|  |  |  | Total Qty |  | 10831 | Cft
C-19 | P.C.C Under plinth
| P C C Class D | 1 | 10831 |  |  | 10831
|  |  |  | Total Qty |  | 10831 | Cft
C-20 | PCC 1:4:8 | 1 | 470 |  |  | 470 | Cft
C-21 | RCC 1:2:4 | 1 | 1175 |  |  | 1175 | Cft
C-22 | Steel G-40 | 1 | 4265 |  |  | 4265 | KG
C-23 | Aluminium sheet for Expansion Joint | 1 | 2100 |  |  | 2100 | Sft
C-24 | Aluminium sheet for Expansion Joint | 1 | 2100 |  |  | 2100 | Sft
C-25 | Form Work Horizontal | 1 | 3024 |  |  | 3024 | Sft
C-26 | Form Work Vertical | 1 | 6048 |  |  | 6048 | Sft
C-27 | G.FLOOR BRICK WORK
4.5" Brick WORK
| G.Floor | 1 | 1640 |  |  | 1640
|  |  |  | Total Qty |  | 1640 | Cft
C-28 | Brick Work First Floor | 1 | 2800 |  |  | 2800 | Cft
C-29 | Brick Work 2nd Floor | 1 | 50 |  |  | 50 | Cft
C-30 | Hollow Block 4" | 1 | 210 |  |  | 210 | Cft
C-31 | Hollow Block 8" | 1 | 241 |  |  | 241 | Cft
C-32 | Solid Block 4" | 1 | 210 |  |  | 210 | Cft
C-33 | Solid Block 8" | 1 | 241 |  |  | 241 | Cft
C-34 | Khura on Roof | 1 | 8 |  |  | 8 | Each
C-35
C-36 | Grouting 4.5" | 1 | 310 |  |  | 310 | Cft
C-37 | P.C.C Coloured Tile for Plinth Protection
| Plinth.P Area | 1 | 10033 |  |  | 10033
|  |  |  | Total Qty |  | 10033 | Sft
C-38 | Terrazo Tile Flooring
|  | 1 | 3500 |  |  | 3500
|  |  |  | Total Qty |  | 3500 | Sft
C-39 | Mosaic Marble Chips | 1 | 3133 |  |  | 3133
C-40 | Landing | 1 | 175 |  |  | 175
|  |  |  | Total Qty |  | 175 | Sft
C-41 | Tread | 1 | 642 | 1 |  | 642
|  |  |  | Total Qty |  | 642 | Sft
C-42 | 3/4" Thick Counter Marble/ Granite
| Recipition Counter Top | 1 | 2469 |  |  | 2469
|  |  |  | Total Qty |  | 2469 | Sft
C-43 | 3/4" Thick Counter Marble / Granite
|  | 1 | 2469 |  |  | 2469 | Sft
C-44 | 3/4" Thick Counter/Vanity Marble
| Toilet counter | 1 | 1373 |  |  | 1373
|  |  |  | Total Qty |  | 1373 | Sft
C-45 | 3/4" Thick Counter Marble
G.F
Kitchen Counter
| " | 1 | 440 |  |  | 440
|  |  |  | Total Qty |  | 440 | Sft
C-46 | Mosaic Dado Skirting Elevated water Tank Walls | 1 | 7500 |  |  | 7500 | Sft
C-47 | Marble Dado / Skirting | 1 | 109 |  |  | 109 | Sft
C-48 | Ramp Flooring Vinyle Tile
Main Ramp
Entrance
|  | 1 | 3175 |  |  | 3175
|  |  |  | Total Qty |  | 3175 | Sft
C-49 | Pocelain ( Floor Tile ) 16"x 16"
|  | 1 | 5931 |  |  | 5931 | Sft
C-50 | Porcelain Tile Dado up to 4' Height and Floor
|  | 1 | 59915 |  |  | 59915 | Sft
C-51 | Granite Tile flooring
| Recipition Counter wall | 1 | 787 |  |  | 787 | Sft
C-52 | Chemical Polishig of Marble Dado | 1 | 109 |  |  | 109 | Sft
C-53 | 1/2" Thick internal plaster up to 20' height
|  | 1 | 116038 |  |  | 116038 | Sft
C-54 | Cement Plaster 20' to 30' 1/2" | 1 | 22806 |  |  | 22806
C-55 | Cement Plaster 20' heigh 3/4" | 1 | 55040 |  |  | 55040 | Sft
C-56 | Cement Plaster 20' to 30' 3/4" | 1 | 13170 |  |  | 13170 | Sft
C-57 | 3/8" Thick Under Soffit / Ceiling Plaster
|  | 1 | 1816 |  |  | 1816
|  |  |  | Total Qty |  | 1816 | Sft
C-58 | 3/8" Thick Under Soffit / Ceiling Plaster
|  | 1 | 1933 |  |  | 1933 | Sft
C-59 | Prime Coat of Chalk Under Distemper | 1 | 35385 |  |  | 35385 | Sft
C-60 | Wall Putty | 1 | 35385 |  |  | 35385 | Sft
C-61 | Distemper Paint New Surface
|  | 1 | 35385 |  |  | 35385 | Sft
C-62 | Distemper Paint Old Surface
|  | 1 | 41653 |  |  | 41653 | Sft
|  |  |  | Total Qty |  | 41653
C-63 | Grooved Cement Sand Plaster over Roughened plaster | 1 | 55040 |  |  | 55040 | Sft
C-64 | Grooved Cement Sand Plaster over Roughened plaster | 1 | 13710 |  |  | 13710 | Sft
C-65 | Expanded Metal
| Cement Plaster Qty | 1 | 27554 |  |  | 27554
|  |  |  | Total |  | 27554
|  |  |  | Total Qty |  | 27554 | Sft
C-66 | Door Closer
| DW-1 | 165 |  |  |  | 165
|  |  |  | Total Qty |  | 165 | NO'S
C-67 | Rim Lock
| G.Floor | 165 |  |  |  | 165
|  |  |  | Total Qty |  | 165 | NO'S
C-68 | Mineral Fiber Ceiling | 1 | 100 |  |  | 100
C-69 | Wooden Pannel Door SL
|  | 1 | 5336 |  |  | 5336
|  |  |  | Total Qty |  | 5336 | Sft
C-70 | Kick Plate
|  | 671 |  |  |  | 671
|  |  |  | Total Qty |  | 671 | Rft
C-71 | Aluminum fixed Window
|  | 1 | 851 |  |  | 851
C-72 | Aluminum Sliding Window
G. FLOOR
| W-2 | 1 | 7336 |  |  | 7336 | Sft
|  |  |  | Total Qty |  | 7336 | Sft
C-73 | Aluminum Window Fly screen
| W-2 | 1 | 3668 |  |  | 3668
|  |  |  | Total Qty |  | 3668 | Sft
0
C-74 | Aluminum Door DL
G. FLOOR
|  | 1 | 1380 |  |  | 1380
|  |  |  | Total Qty |  | 1380 | Sft
C-75 | Floor mounted Cabinet in Kitchen
| Kitchen | 1 | 108 |  |  | 108
|  |  |  | Total |  | 108
|  |  |  | Total Qty |  | 108 | Sft
C-76 | Wall Cabinet in Kitchen
| Kitchen | 1 | 72 | 1 |  | 72
|  |  |  | Total Qty |  | 72 | Sft
C-77 | UPVC Door
|  | 1 | 2419 |  |  | 2419
|  |  |  | Total Qty |  | 2419 | Sft
C-78 | Door Paint / polish
G.FLOOR
D-1
D-6
|  | 1 | 10673 |  |  | 10673
|  |  |  | Total Qty |  | 10674 | Sft
C-79 | Emulsion Paint First Coat
|  | 1 | 117698 |  |  | 117698
C-80 | Emulsion Paint 2nd Coat | 1 | 235396 |  |  | 235396
C-81 | Weather Shield 1ST First Coat | 1 | 67313 |  |  | 67313
C82 | Weather Shield 1ST 2nd Coat | 1 | 67313 |  |  | 67313
C-83 | Weather Shield 1ST 3rd Coat | 1 | 67313 |  |  | 67313
C-84 | Heavy Steel Work | 1 | 8 |  |  | 80
C-85 | Trusses, Staging of water tanks | 1 | 8 |  |  | 8
|  |  |  | Total Qty |  | 8 | Rft
C-86 | Collapsible gate
| W-2 | 1 | 80 |  |  | 80
|  |  |  | Total |  | 80
|  |  |  | Total Qty |  | 80 | Sft
C-87 | SS Railing
|  | 1 | 936 |  |  | 936
C-88 | MS Grill | 1 | 9910 |  |  | 9910
C-89 | Steel Door
|  | 1 | 120 |  |  | 120
0
|  |  |  | Total |  | 120
|  |  |  | Total Qty |  | 120 | Sft
C-90 | Cleaning of Water Tank | 1 | 55000 |  |  | 55000 | Per Gallon
C-91 | Termite Treatment
|  | 1 | 8565 |  |  | 8565
C-92 | Steel Nails
|  | 1 | 11790 |  |  | 11790
Dismantaling of floor & Wall Tile
Sft
C-93 | Dismantling / Disposal Wall tiles
|  | 1 | 162147 |  |  | 162147 | Sft
C-94 | Dismantling / Disposal / Plinth Protection
|  | 1 | 11789 |  |  | 11789
C-95 | Dismantling / removal Roof Treatment
|  | 1 | 67537 |  |  | 67537
C-96 | Dismantling / Stacking of Reinforcement | 1 | 100 |  |  | 100
C-97 | Dismantling of RCC Concrete
|  | 1 | 100 |  |  | 100
C-98 | Removal of Plaster
|  | 1 | 138844 |  |  | 138844
C-99 | Removal and Stacking False Ceiling incl Lead And Lift
|  | 1 | 61440 |  |  | 61440
C-100 | Removal and Stacking Of any type of Door / Window/ vent/ Skylight/Grill including rcc element and masonary work incl lesd and lift | 1 | 17322 |  |  | 17322
C-101 | Dismantling of Conduit on Surface | 1 | 3590 |  |  | 3590
C-102 | Dismantling of Conduit Recessed in Wall | 1 | 21540 |  |  | 21540
C-103 | Dismantling of WC'S Asian
|  | 1 | 270 |  |  | 270
C-104 | Dismantling of WC'S European
|  | 1 | 2160 |  |  | 2160
C-105 | Creating Holes in Slabs
|  | 1 | 9 |  |  | 9
C-106 | Providing and laying 1:3:6 Concrete in Sub Column on any floor | 1 | 1000 |  |  | 1000
C-107 | Water Proofing Membrane
|  | 1 | 67537 |  |  | 67537
C-108 | Plan G.i Sheet
|  | 1 | 135074 |  |  | 135074
C-109 | Plan G.i Sheet
|  | 1 | 1150 |  |  | 1150
C-110 | Porcelain (Wall tile) 16" x 16"
|  | 1 | 24629 |  |  | 24629
|  |  |  | Total Qty |  | 24629 | Sft
C-111 | Porcelain Tile Flooring
|  | 1 | 59915 |  |  | 59915
|  |  |  | Total Qty |  | 59915 | Sft
#REF!
C-112 | Marble Riser / dado / skirting
|  | 1 | 363 |  |  | 363
C-113 | 3/4" Granite Red Rubi
|  | 1 | 400 |  |  | 400
Epoxy flooring
C-114
| X-RAY | 1 | 2765 |  |  | 2765
|  |  |  | Total |  | 2765
|  |  |  | Total Qty |  | 2765
C-115 | Epoxy Painting
|  | 1 | 3337 |  |  | 3337 | Sft
C-116 | Matt Enamel / Antibacterial Paint Inner Walls
|  | 1 | 124946 |  |  | 124946
|  |  |  | Total Qty |  | 124946 | Sft
C-117 | X-RAY Room Wall
| Lead Lining 3/4" overlaid by laminated sheet board | 1 | 70 |  | 11.5 | 805
|  |  |  | Total |  | 805
|  |  |  | add 5% |  | 40.25
|  |  |  | Total Qty |  | 845.25 | Sft
C-118 | Lead Lining
|  | 1 | 150 |  |  | 150
C-119 | Dry Partition
|  | 1 | 400 |  |  | 400
C-120 | 12mm Temperd glass
|  | 1 | 150 |  |  | 150
C-121 | FRD
|  | 1 | 2 |  |  | 2
C-122 | Hermatic Door
|  | 1 | 2 |  |  | 2
C-123 | Aluminium False Ceiling
|  | 1 | 73092 |  |  | 73092
|  |  |  | Total Qty |  | 73092 | Sft
C-124 | UPVC Bumper Rail | 1 | 11302 |  |  | 11302
|  |  |  | Total Qty |  | 11302 | Rft
C-125 | Pvc Paneling
|  | 1 | 2500 |  |  | 2500 | Sft
C-126 | ACP
|  | 1 | 940 |  |  | 940 | Sft
C-127 | Color Crete
|  | 1 | 64003 |  |  | 64003 | Sft
C-128 | Nano Quartz
|  | 1 | 2500 |  |  | 2500 | Sft
C-129 | G.I Flashing Type -1 | 1 | 1000 |  |  | 1000 | Rft
C-130 | G.I Flashing Type -2 | 1 | 1000 |  |  | 1000 | Rft
C-131 | G.I Flashing Type -3 | 1 | 1000 |  |  | 1000 | Rft
C-132 | G.I Flashing Type -4 | 1 | 1000 |  |  | 1000 | Rft
C-133 | Sealent-1 | 1 | 4000 |  |  | 4000 | Rft
C-134 | Sealent-2
|  | 1 | 1000 |  |  | 1000 | Rft
C-135 | SBR Chemical
|  | 1 | 103797 |  |  | 103797 | Sft
C-136 | External Signage and Internal Signage
|  | 1 | 1 |  |  | 1 | Job
C-137 | Wall Graphics
|  | 1 | 750 |  |  | 750 | Sft
C-138 | S.S Edge Protection
|  | 1 | 500 |  |  | 500 | Rft
C-139 | Sika Seal
|  | 1 | 67537 |  |  | 67537 | Sft